## Frame formats(TCP)
Frame formats
The Sinexcel Energy Storage Inverters support RS485(MODBUS RTU) or Ethernet(MODBUS TCP/IP)， When implementing RS485, the bode rate is 19200bps or 9600bps, verification: MODBUS RTU CRC16 When deploying ethernet, the communication format conforms to MODBUS TCP.
Refer to the attached document for more information about MODBUS TCP/IP
Table 1 MBAP header
Fields | Length | Description |  | Client | Server
Transaction Identifier | 2 Bytes | Indentification of a MODBUS request/response transaction |  | Initialized by the client | Recopied by the server from the received request
Protocol Identifier | 2 Bytes | 0= MODBUS protocol |  | Initialized by the client | Recopied by the server from the received request
Length | 2 Bytes | Number of following Bytes |  | Initialized by the client(request) | Initialized by the server(response)
Unit Identifier | 1 Byte | Identification of a remote slave connected on a serial line or on other buses |  | Initialized by the client | Recopied by the server from the received request
Table 2 Function code list
Function Code | Function
01 | Read coil status(output relay)
02 | Read input status(input relay)
03 | read holding registers(output register)
04 | read input registers
05 | Force single coil
06 | Preset single register
07 | read exception status
08 | Diagnostics
15 | Force multiple coils
16 | Preset multiple registers
101 | For self-defining
Table 3 Exception code list
Exception Code | MODBUS name | Comments
01 | Illegal Function Code | The function code is unknown by the server
02 | Illegal Data Address | Dependant on the request
03 | Illegal Data Value | Dependant on the request
04 | Server Failure | The server failed during the execution
05 | Acknowledge | The server accepted the service invocation but the service requires a relatively long time to execute. The server therefore returns only an acknowledgement of the service invocation receipt.
06 | Server Busy | The server was unable to accept the MB Request PDU. The client application has the responsibility of deciding if and when to re-send the request.
F0 | Controlling method Error | Remote control not supported
Table 4.1 Reading data request
MBAP | Function code | Data Field
7 Bytes | 1 Byte | Byte1~2 | Byte3~4
|  | Starting Address of register | Quantity of registers
Table 4.2 Reading successful response
MBAP | Function Code | Data Field
7 Bytes | 1 Byte | Byte 1 | Byte 2~3 | Byte 4~5 | … | Byte 2N~2N+1
|  | Quantity of Data Bytes | Data 1 | Data 2 | … | Data N
Table 4.3 Reading failed response
MBAP | Error Code |  | Exeption code
7 Bytes | 1 Byte |  | 1 Byte
| Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3
Table 5.1 Writing Data request(Writing multiple values)
MBAP | Function Code | Data Field
7 Bytes | 1 Byte | Byte 1~2 | Byte 3~4 | Byte 6~7 | Byte 8~9 | … | Byte 2N+4~2N+5
|  | Starting Address of register | Quantity of registers | Data 1 | Data 2 |  | Data N
Table 5.2 Writing successful response(Writing multiple values)
MBAP | Function Code | Data Field
7 Bytes | 1 Byte | Byte 1~2 | Byte 3
|  | Starting Address of register | Quantity of Data Bytes
Table 5.3 Writing failed response(Writing multiple values)
MBAP | Error Code |  | Exeption code
7 Bytes | 1 Byte |  | 1 Byte
| Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3
Table 6.1 Writing Data request(Writing single value)
MBAP | Function Code | Data Field
7 Bytes | 1 Byte | Byte 1~2 | Byte 3~4
|  | Starting Address of register | Data
Table 6.2 Writing successful response(Writing single value)
MBAP | Function Code | Data Field
7 Bytes | 1 Byte | Byte 1~2 | Byte 3~4
|  | Starting Address of register | Data
Table 6.3 Writing failed response(Writing single value)
MBAP | Error Code |  | Exeption code
7 Bytes | 1 Byte |  | 1 Byte
| Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3
Table 7 Applied Function code list by Sinexcel
Function | Function Code | register range | Remark
Read-only register | 0x03 or 0x04 | 53000~53099(RO) | Status and alarm parameters of equipment(PCS)
|  | 53100~53199(RO) | Status and alarm parameters of equipment(STS)
|  | 53200~53499(RO) | Analog quantity of equipment(PCS)
|  | 53500~53599(RO) | Analog quantity of equipment(STS)
Read-write register | 0x06(W) 0x03 or 0x04(R) | 53600~53899(R/W) | Setting-up parameters of equipment
Write register | 0x06 | 53900~53999(W) | Control parameters of equipment
| 0x10 | 0xF000(W) | Monitoring Setting-up parameters of equipment: RTC Setting

## Frame formats(RTU)
Frame formats
The Sinexcel Energy Storage Inverters support RS485(MODBUS RTU) or Ethernet(MODBUS TCP/IP)， When implementing RS485, the bode rate is 19200bps or 9600bps, verification: MODBUS RTU CRC16 When deploying ethernet, the communication format conforms to MODBUS TCP.
MODBUS RTU
Table 1 Device Address
Fields | Length | Range
Device Address | 1 Bytes | 1~0xFF
Table 2 Function code list
Function Code | Function
01 | Read coil status(output relay)
02 | Read input status(input relay)
03 | read holding registers(output register)
04 | read input registers
05 | Force single coil
06 | Preset single register
07 | read exception status
08 | Diagnostics
15 | Force multiple coils
16 | Preset multiple registers
101 | For self-defining
Table 3 Exception code list
Exception Code | MODBUS name | Comments
01 | Illegal Function Code | The function code is unknown by the server
02 | Illegal Data Address | Dependant on the request
03 | Illegal Data Value | Dependant on the request
04 | Server Failure | The server failed during the execution
05 | Acknowledge | The server accepted the service invocation but the service requires a relatively long time to execute. The server therefore returns only an acknowledgement of the service invocation receipt.
06 | Server Busy | The server was unable to accept the MB Request PDU. The client application has the responsibility of deciding if and when to re-send the request.
F0 | Controlling method Error | Remote control not supported
Table 4.1 Reading data request
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x03/0x04 | 0x00 | 0x00 | 0x00 | 0x0A | CRC
Table 4.2 Reading successful response
Device address | Operation code | data quantily | data 1 | …… | data N | Verification
|  | (register quantity*2) |  |  |  | (L->H)
0x01 | 0x03/0x04 | 0x14(N) | XX | …… | XX | CRC
Table 4.3 Reading failed response
Device address | Error Code |  | Exeption code |  |  | Verification
| 1 Byte |  | 1 Byte |  |  | (L->H)
0x01 | Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3 |  |  | CRC
Table 5.1 Writing Data request(Writing multiple values)
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | data quantity | set data(1-6) | Verification
(L->H)
0x01 | 0x10 | 0xF0 | 0x00 | 0x00 | 0x03 | 0x06 | …… | CRC
Table 5.2 Writing successful response(Writing multiple values)
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x10 | 0xF0 | 0x00 | 0x00 | 0x03 | CRC
Table 5.3 Writing failed response(Writing multiple values)
Device address | Error Code |  | Exeption code |  |  | Verification
| 1 Byte |  | 1 Byte |  |  | (L->H)
0x01 | Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3 |  |  | CRC
Table 6.1 Writing Data request(Writing single value)
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC
Table 6.2 Writing successful response(Writing single value)
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC
Table 6.3 Writing failed response(Writing single value)
Device address | Error Code |  | Exeption code |  |  | Verification
| 1 Byte |  | 1 Byte |  |  | (L->H)
0x01 | Error Code=Function Code+0x80 |  | 01 or 02 or 03 or 04, refer to Table 3 |  |  | CRC
Table 7 Applied Function code list by Sinexcel
Function | Function Code | register range | Remark
Read-only register | 0x03 or 0x04 | 53000~53099(RO) | Status and alarm parameters of equipment(PCS)
|  | 53100~53199(RO) | Status and alarm parameters of equipment(STS)
|  | 53200~53499(RO) | Analog quantity of equipment(PCS)
|  | 53500~53599(RO) | Analog quantity of equipment(STS)
Read-write register | 0x06(W) 0x03 or 0x04(R) | 53600~53899(R/W) | Setting-up parameters of equipment
Write register | 0x06 | 53900~53999(W) | Control parameters of equipment
| 0x10 | 0xF000(W) | Monitoring Setting-up parameters of equipment: RTC Setting

## RO registers-Client
Model → |  | PWS1 | Standard | without STS | * | NONONO | NONONO | *PWS1* | *NONONO* | *NONONO*
Address | Size | Access | Register Name | 寄存器名称(Register Name in Chinese) | Type | Range 1.Fault: PCS shutdown 2.Alarm: PCS still work | offset | Accuracy | Unit | Comments: Function Code: 0x03 or ox04 (Actual Value = Value * Accuracy + Offset)
53000 | bit0 | RO | AC-Group: AC bus over voltage | AC模块组: 交流母线过压 | / | 0: Normal, 1: Fault | / | / | / |  | /
53000 | bit1 | RO | AC-Group: AC bus over frequency | AC模块组: 交流母线过频 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit2 | RO | AC-Group: AC bus under voltage | AC模块组: 交流母线欠压 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit3 | RO | AC-Group: islanding protection | AC模块组: 逆变器孤岛保护 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit4 | RO | AC-Group: DC input over voltage | AC模块组: 直流输入过压 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit5 | RO | AC-Group: On/Off-grid toggling error | AC模块组: 并离网切换错误 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit6 | RO | AC-Group: AC phase reversed | AC模块组: 交流反序 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit7 | RO | AC-Group: DC input under voltage | AC模块组: 直流输入欠压 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit8 | RO | AC-Group: Overload alarm | AC模块组: 过载报警 | / | 0: Normal, 1: Alarm | / | / | /
53000 | bit9 | RO | AC-Group: AC bus voltage Abnormal | AC模块组: 交流母线电压异常 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit10 | RO | AC-Group: AC phase lost | AC模块组: 交流缺相 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit11 | RO | AC-Group: AC bus voltage asymmetric | AC模块组: 交流母线电压不平衡 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit12 | RO | AC-Group: AC bus under frequency | AC模块组: 交流母线欠频 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit13 | RO | AC-Group: Battery under energy | AC模块组: 电池电量不足 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit14 | RO | AC-Group: DC input over current | AC模块组: 直流输入过流 | / | 0: Normal, 1: Fault | / | / | /
53000 | bit15 | RO | AC-Group: Off-grid Volt phase reversed | AC模块组: 离网电压反序 | / | 0: Normal, 1: Fault | / | / | /
53001 | bit0 | RO | AC-Group: PLL fault | AC模块组: 锁相失败 | / | 0: Normal, 1: Fault | / | / | /
53001 | bit1 | RO | AC-Group: Ambient over temperature | AC模块组: 环境温度过温 | / | 0: Normal, 1: Alarm | / | / | /
53001 | bit2 | RO | AC-Group: Ambient temp. sensor fault | AC模块组: 环温探头故障 | / | 0: Normal, 1: Fault | / | / | /
53001 | bit3 | RO | AC-Group: Cabinet temp. sensor fault | AC模块组: 柜温探头故障 | / | 0: Normal, 1: Fault | / | / | /
53001 | bit4 | RO | AC-Group: Cabinet over temperature | AC模块组: 机柜温度过温 | / | 0: Normal, 1: Fault | / | / | /
53001 | bit5 | RO | AC-Group: Off-grid voltage phase lost | AC模块组: 离网电压缺相 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit0 | RO | AC-Group: 24V auxiliary power Fault | AC模块组: 24V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit1 | RO | AC-Group: emergency stopped(EPO) | AC模块组: 紧急停机 | / | 0: Normal, 1: Fault | / | / | / | EPO button pressed
53002 | bit2 | RO | AC-Group: Grounding fault | AC模块组: 接地故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit3 | RO | AC-Group: DC bus over voltage | AC模块组: 直流母线过压 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit4 | RO | AC-Group: Module over temperature | AC模块组: 模块温度过温 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit5 | RO | AC-Group: Module current asymmetric | AC模块组: 模块电流不平衡 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit6 | RO | AC-Group: Fan Fault | AC模块组: 风扇故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit7 | RO | AC-Group: DC relay open circuit | AC模块组: 直流继电器开路 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit8 | RO | AC-Group: Calibration parameter Abnormal | AC模块组: 校准参数异常 | / | 0: Normal, 1: Alarm | / | / | /
53002 | bit9 | RO | AC-Group: Bus voltage unbalanced | AC模块组: 母线电压不平衡 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit10 | RO | AC-Group: Fuse blown | AC模块组: 保险故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit11 | RO | AC-Group: DSP initializing fault | AC模块组: DSP初始化故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit12 | RO | AC-Group: DC soft start failed | AC模块组: 直流软启动失败 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit13 | RO | AC-Group: CAN A comm. Fault | AC模块组: CANA通讯故障 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit14 | RO | AC-Group: DC input reversed | AC模块组: 直流输入反接 | / | 0: Normal, 1: Fault | / | / | /
53002 | bit15 | RO | AC-Group: AC current DC component Abnormal | AC模块组: 交流电流直流分量异常 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit0 | RO | AC-Group: Transformer over temp. | AC模块组: 变压器过温 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit1 | RO | AC-Group: U2 comm. 2 Abnormal | AC模块组: U2通信异常2 | / | 0: Normal, 1: Alarm | / | / | /
53003 | bit2 | RO | AC-Group: Tripped by BMS or DC switch | AC模块组: BMS故障或直流开关断开 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit3 | RO | AC-Group: SPD fault | AC模块组: 防雷器故障 | / | 0: Normal, 1: Alarm | / | / | /
53003 | bit4 | RO | AC-Group: Overload timeout fault | AC模块组: 过载超时故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit5 | RO | AC-Group: AC soft start failed | AC模块组: 交流软启动失败 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit6 | RO | AC-Group: Synchronous signal 1 fault | AC模块组: 同步信号故障1 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit7 | RO | AC-Group: DSP version fault | AC模块组: DSP版本故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit8 | RO | AC-Group: AC relay open circuit | AC模块组: 交流继电器开路 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit9 | RO | AC-Group: Sampling zero Abnormal | AC模块组: 采样零点异常 | / | 0: Normal, 1: Alarm | / | / | /
53003 | bit10 | RO | AC-Group: U2 comm. 1 Abnormal | AC模块组: U2通信异常1 | / | 0: Normal, 1: Alarm | / | / | /
53003 | bit11 | RO | AC-Group: 15V auxiliary power Fault | AC模块组: 15V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit12 | RO | AC-Group: Module ID reduplicated | AC模块组: 模块重号故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit13 | RO | AC-Group: RS485 comm. Fault | AC模块组: RS485通讯故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit14 | RO | AC-Group: CAN B comm. Fault | AC模块组: CANB通讯故障 | / | 0: Normal, 1: Fault | / | / | /
53003 | bit15 | RO | AC-Group: Restart too much | AC模块组: 重启过多 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit0 | RO | AC-Group: CPLD version Fault | AC模块组: CPLD版本故障 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit1 | RO | AC-Group: Hardware version Fault | AC模块组: 硬件版本故障 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit2 | RO | AC-Group: DC relay short circuit | AC模块组: 直流继电器短路 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit3 | RO | AC-Group: DC bus under voltage | AC模块组: 直流母线欠压 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit4 | RO | AC-Group: AC relay short circuit | AC模块组: 交流继电器短路 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit5 | RO | AC-Group: Synchronous signal 2 fault | AC模块组: 同步信号故障2 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit6 | RO | AC-Group: Parameter mismatch | AC模块组: 参数不匹配 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit7 | RO | AC-Group: CAN C comm. Fault | AC模块组: CANC通讯故障 | / | 0: Normal, 1: Alarm | / | / | /
53004 | bit8 | RO | AC-Group: Ambient humidity too high | AC模块组: 环境湿度过高 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit9 | RO | AC-Group: BMS voltage Abnormal | AC模块组: BMS电压异常 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit10 | RO | AC-Group: BMS current Abnormal | AC模块组: BMS电流异常 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit11 | RO | AC-Group: BMS temperature Abnormal | AC模块组: BMS温度异常 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit12 | RO | AC-Group: BMS shutdown | AC模块组: BMS跳机 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit13 | RO | AC-Group: Insulation detection Abnormal | AC模块组: 绝缘检测异常 | / | 0: Normal, 1: Fault | / | / | /
53004 | bit14 | RO | AC-Group: Hardware sampling Abnormal | AC模块组: 硬件采样异常 | / | 0: Normal, 1: Fault | / | / | /
53009 | bit4 | RO | PCS: PE-N contactor short circuit | PCS: PE-N接触器短路 | / | 0: Normal, 1: Fault | / | / | /
53009 | bit5 | RO | PCS: PE-N contactor open circuit | PCS: PE-N接触器开路 | / | 0: Normal, 1: Fault | / | / | /
53009 | bit6 | RO | PCS: Neutral contactor short circuit | PCS: N接触器短路 | / | 0: Normal, 1: Fault | / | / | /
53009 | bit7 | RO | PCS: Neutral contactor open circuit | PCS: N接触器开路 | / | 0: Normal, 1: Fault | / | / | /
53010 | bit0 | RO | AC-Group: On/Off status | AC模块组: 启停状态 | / | 0: Stop, 1: Running | / | / | /
53010 | bit1 | RO | Standby status | 待机状态 | / | 0: False, 1: True | / | / | /
53010 | bit2 | RO | Grid-tied status | 并网状态 | / | 0: False, 1: True | / | / | /
53010 | bit3 | RO | Off-grid status | 离网状态 | / | 0: False, 1: True | / | / | /
53010 | bit8 | RO | Local manual control | 本地手动控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS will NOT respond to remote controlling
53010 | bit9 | RO | Local auto control | 本地自动控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS will NOT respond to remote controlling
53010 | bit10 | RO | Remote control | 远程控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS Will respond to remote controlling
53011 | bit0 | RO | AC dispatch mode enabled | 交流调度模式使能 | / | 0: False, 1: True | / | / | / | Making AC port the controlling target
53011 | bit1 | RO | DC dispatch mode enabled | 直流调度模式使能 | / | 0: False, 1: True | / | / | / | Making DC port the controlling target
53011 | bit2 | RO | FVRT enabled | 穿越使能 | / | 0: False, 1: True | / | / | /
53011 | bit3 | RO | Island detection enable | 孤岛检测使能 | / | 0: False, 1: True | / | / | /
53011 | bit8 | RO | Ac switch closed | 交流开关闭合 | / | 0: Open, 1: Closed | / | / | /
53011 | bit9 | RO | Alrm status | 告警状态 | / | 0: False, 1: True | / | / | /
53011 | bit10 | RO | Fault status | 故障状态 | / | 0: False, 1: True | / | / | /
53011 | bit12 | RO | PCS initialization status | PCS初始化状态 | / | 0: Unfinished, 1: Finished | / | / | /
53013 | bit0 | RO | DC String 1: battery fully charged | 直流支路1: 电池充满 | / | 0: False, 1: True | / | / | /
53013 | bit1 | RO | DC String 1: battery totally discharged | 直流支路1: 电池放空 | / | 0: False, 1: True | / | / | /
53013 | bit2 | RO | DC String 1: charging | 直流支路1: 充电 | / | 0: False, 1: True | / | / | /
53013 | bit3 | RO | DC String 1: discharging | 直流支路1: 放电 | / | 0: False, 1: True | / | / | /
53013 | bit4 | RO | DC String 1: PV generating | 直流支路1: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types
53013 | bit5 | RO | DC String 1: PV sleeping | 直流支路1: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types
53013 | bit6 | RO | DC String 1: battery constant voltage topping charging | 直流支路1: 电池恒压均充 | / | 0: False, 1: True | / | / | /
53013 | bit7 | RO | DC String 1: battery constant voltage float charging | 直流支路1: 电池恒压浮充 | / | 0: False, 1: True | / | / | /
53013 | bit8 | RO | DC String 1: DC switch status | 直流支路1: 直流开关状态 | / | 0: Open, 1: Closed | / | / | /
53013 | bit9 | RO | DC String 1: PV MPPT | 直流支路1: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types
53013 | bit10~12 | RO | DC String 1: Insulation detection status | 直流支路1: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4；
53014 | bit0 | RO | DC String 1: On/Off status | 直流支路1: 启停状态 | / | 0: Stop, 1: Running | / | / | /
53025 | bit0 | RO | AC-Group: module 1 online | AC模块组: 模块1在线 | / | 0: False, 1: True | / | / | /
53025 | bit1 | RO | AC-Group: module 2 online | AC模块组: 模块2在线 | / | 0: False, 1: True | / | / | /
53025 | bit2 | RO | AC-Group: module 3 online | AC模块组: 模块3在线 | / | 0: False, 1: True | / | / | /
53025 | bit3 | RO | AC-Group: module 4 online | AC模块组: 模块4在线 | / | 0: False, 1: True | / | / | /
53025 | bit4 | RO | AC-Group: module 5 online | AC模块组: 模块5在线 | / | 0: False, 1: True | / | / | /
53025 | bit5 | RO | AC-Group: module 6 online | AC模块组: 模块6在线 | / | 0: False, 1: True | / | / | /
53025 | bit6 | RO | AC-Group: module 7 online | AC模块组: 模块7在线 | / | 0: False, 1: True | / | / | /
53025 | bit7 | RO | AC-Group: module 8 online | AC模块组: 模块8在线 | / | 0: False, 1: True | / | / | /
53025 | bit8 | RO | AC-Group: module 9 online | AC模块组: 模块9在线 | / | 0: False, 1: True | / | / | /
53025 | bit9 | RO | AC-Group: module 10 online | AC模块组: 模块10在线 | / | 0: False, 1: True | / | / | /
53025 | bit10 | RO | Rack Func board online | 机架功能板在线 | / | 0: False, 1: True | / | / | /
53027 | bit0 | RO | AC-Group: module 1 running | AC模块组: 模块1运行 | / | 0: False, 1: True | / | / | /
53027 | bit1 | RO | AC-Group: module 2 running | AC模块组: 模块2运行 | / | 0: False, 1: True | / | / | /
53027 | bit2 | RO | AC-Group: module 3 running | AC模块组: 模块3运行 | / | 0: False, 1: True | / | / | /
53027 | bit3 | RO | AC-Group: module 4 running | AC模块组: 模块4运行 | / | 0: False, 1: True | / | / | /
53027 | bit4 | RO | AC-Group: module 5 running | AC模块组: 模块5运行 | / | 0: False, 1: True | / | / | /
53027 | bit5 | RO | AC-Group: module 6 running | AC模块组: 模块6运行 | / | 0: False, 1: True | / | / | /
53027 | bit6 | RO | AC-Group: module 7 running | AC模块组: 模块7运行 | / | 0: False, 1: True | / | / | /
53027 | bit7 | RO | AC-Group: module 8 running | AC模块组: 模块8运行 | / | 0: False, 1: True | / | / | /
53027 | bit8 | RO | AC-Group: module 9 running | AC模块组: 模块9运行 | / | 0: False, 1: True | / | / | /
53027 | bit9 | RO | AC-Group: module 10 running | AC模块组: 模块10运行 | / | 0: False, 1: True | / | / | /
53029 | bit0 | RO | AC-Group: module 1 Alarm | AC模块组: 模块1告警 | / | 0: False, 1: True | / | / | /
53029 | bit1 | RO | AC-Group: module 2 Alarm | AC模块组: 模块2告警 | / | 0: False, 1: True | / | / | /
53029 | bit2 | RO | AC-Group: module 3 Alarm | AC模块组: 模块3告警 | / | 0: False, 1: True | / | / | /
53029 | bit3 | RO | AC-Group: module 4 Alarm | AC模块组: 模块4告警 | / | 0: False, 1: True | / | / | /
53029 | bit4 | RO | AC-Group: module 5 Alarm | AC模块组: 模块5告警 | / | 0: False, 1: True | / | / | /
53029 | bit5 | RO | AC-Group: module 6 Alarm | AC模块组: 模块6告警 | / | 0: False, 1: True | / | / | /
53029 | bit6 | RO | AC-Group: module 7 Alarm | AC模块组: 模块7告警 | / | 0: False, 1: True | / | / | /
53029 | bit7 | RO | AC-Group: module 8 Alarm | AC模块组: 模块8告警 | / | 0: False, 1: True | / | / | /
53029 | bit8 | RO | AC-Group: module 9 Alarm | AC模块组: 模块9告警 | / | 0: False, 1: True | / | / | /
53029 | bit9 | RO | AC-Group: module 10 Alarm | AC模块组: 模块10告警 | / | 0: False, 1: True | / | / | /
53029 | bit10 | RO | Rack Func board Alarm | 机架功能板告警 | / | 0: False, 1: True | / | / | /
53031 | bit0 | RO | AC-Group: module 1 fault | AC模块组: 模块1故障 | / | 0: False, 1: True | / | / | /
53031 | bit1 | RO | AC-Group: module 2 fault | AC模块组: 模块2故障 | / | 0: False, 1: True | / | / | /
53031 | bit2 | RO | AC-Group: module 3 fault | AC模块组: 模块3故障 | / | 0: False, 1: True | / | / | /
53031 | bit3 | RO | AC-Group: module 4 fault | AC模块组: 模块4故障 | / | 0: False, 1: True | / | / | /
53031 | bit4 | RO | AC-Group: module 5 fault | AC模块组: 模块5故障 | / | 0: False, 1: True | / | / | /
53031 | bit5 | RO | AC-Group: module 6 fault | AC模块组: 模块6故障 | / | 0: False, 1: True | / | / | /
53031 | bit6 | RO | AC-Group: module 7 fault | AC模块组: 模块7故障 | / | 0: False, 1: True | / | / | /
53031 | bit7 | RO | AC-Group: module 8 fault | AC模块组: 模块8故障 | / | 0: False, 1: True | / | / | /
53031 | bit8 | RO | AC-Group: module 9 fault | AC模块组: 模块9故障 | / | 0: False, 1: True | / | / | /
53031 | bit9 | RO | AC-Group: module 10 fault | AC模块组: 模块10故障 | / | 0: False, 1: True | / | / | /
53031 | bit10 | RO | Rack Func board fault | 机架功能板故障 | / | 0: False, 1: True | / | / | /
53200 | 2 Bytes | RO | AC line voltage L1 to L2 | AB交流线电压 | uint16 | 0~600 | / | 0.1 | V
53201 | 2 Bytes | RO | AC line voltage L2 to L3 | BC交流线电压 | uint16 | 0~600 | / | 0.1 | V
53202 | 2 Bytes | RO | AC line voltage L3 to L1 | CA交流线电压 | uint16 | 0~600 | / | 0.1 | V
53203 | 2 Bytes | RO | AC L1 current | A相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A
53204 | 2 Bytes | RO | AC L2 current | B相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A
53205 | 3 Bytes | RO | AC L3 current | C相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A
53206 | 2 Bytes | RO | AC frequency | 交流频率 | uint16 | 40.00~70.00 | / | 0.01 | Hz
53209 | 2 Bytes | RO | L1 AC active power | A相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW
53210 | 2 Bytes | RO | L2 AC active power | B相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW
53211 | 2 Bytes | RO | L3 AC active power | C相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW
53212 | 2 Bytes | RO | L1 AC reactive power | A相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar
53213 | 2 Bytes | RO | L2 AC reactive power | B相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar
53214 | 2 Bytes | RO | L3 AC reactive power | C相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar
53215 | 2 Bytes | RO | L1 AC apparent power | A相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA
53216 | 2 Bytes | RO | L2 AC apparent power | B相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA
53217 | 2 Bytes | RO | L3 AC apparent power | C相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA
53218 | 2 Bytes | RO | L1 AC PF | A相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01
53219 | 2 Bytes | RO | L2 AC PF | B相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01
53220 | 2 Bytes | RO | L3 AC PF | C相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01
53221 | 2 Bytes | RO | Module temperature | 模块温度 | uint16 | ‐20.0~200.0 | -20 | 0.1 | ℃ | Showing the highest heatsink of the modules
53223 | 2 Bytes | RO | Ambient temperature | 环境温度 | uint16 | ‐20.0~200.0 | -20 | 0.1 | ℃
53224 | 2 Bytes | RO | active power setpoint | 有功功率期望 | uint16 | ‐660.0~660.0 | -660 | 0.1 | kW
53225 | 2 Bytes | RO | reactive power setpoint | 无功功率期望 | uint16 | ‐660.0~660.0 | -660 | 0.1 | kvar
53226 | 2 Bytes | RO | Off-grid voltage regulation setpoint | 离网电压调节期望 | uint16 | ‐0.10~0.10 | -0.1 | 0.01
53227 | 2 Bytes | RO | PF setpoint | PF期望 | uint16 | ‐1.00~1.00 | -1 | 0.01 | /
53235 | 2 Bytes | RO | Total AC active power | 总交流有功功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kW
53236 | 2 Bytes | RO | Total AC reactive power | 总交流无功功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar
53237 | 2 Bytes | RO | Total AC apparent power | 总交流视在功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar
53238 | 2 Bytes | RO | Total AC PF | 总交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01
53239 | 2 Bytes | RO | Accumulative charged energy through AC port Higher 2 bytes | 累积交流充电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh
53240 | 2 Bytes | RO | Accumulative charged energy through AC port Lower 2 bytes | 累积交流充电电量 低两字节 | uint16 |  | / | 1 | kWh
53241 | 2 Bytes | RO | Accumulative discharged energy through AC port higher 2 bytes | 累积交流放电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh
53242 | 2 Bytes | RO | Accumulative discharged energy through AC port lower 2 bytes | 累积交流放电电量 低两字节 | uint16 |  | / | 1 | kWh
53247 | 2 Bytes | RO | Usable capacity | 可用容量 | uint16 | 0~1000.0 |  | 0.1 | kVA
53248 | 2 Bytes | RO | daily charged energy through AC port | 当天交流充电电量 | uint16 | 0~2^16 | / | 1 | kWh
53249 | 2 Bytes | RO | daily discharged energy through AC port | 当天交流放电电量 | uint16 | 0~2^16 | / | 1 | kWh
53250 | 2 Bytes | RO | DC String 1: DC power | 直流支路1: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW
53251 | 2 Bytes | RO | DC String 1: DC voltage | 直流支路1: 直流电压 | uint16 | 0~1000.0 | / | 0.1 | V
53252 | 2 Bytes | RO | DC String 1: DC current | 直流支路1: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A
53257 | 2 Bytes | RO | DC String 1: DC current setpoint | 直流支路1: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A
53258 | 2 Bytes | RO | DC String 1: DC power setpoint | 直流支路1: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW
53590 | 2 Bytes | RO | Monitor soft code | 监控软件代码 | uint16 | 0~2^16 | / | 1 | /
53591 | 2 Bytes | RO | AC soft code | AC软件代码 | uint16 | 0~2^16 | / | 1 | /
53592 | 2 Bytes | RO | DC soft code | DC软件代码 | uint16 | 0~2^16 | / | 1 | /
53593 | 2 Bytes | RO | U2 soft code | U2软件代码 | uint16 | 0~2^16 | / | 1 | /
53594 | 2 Bytes | RO | STS soft code | STS软件代码 | uint16 | 0~2^16 | / | 1 | /

## RW registers-Client
Model → |  | PWS1 | Standard | without STS | * | NONONO | NONONO | *PWS1* | *NONONO* | *NONONO*
Address | Size | Access | Register Name | 寄存器名称(Register Name in Chinese) | Type | Range | Offset | Accuracy | Unit | Comments Function Code: 0x06(W), 0x03(R) (No Offset)
53600 | 2 Bytes | RW | Grid interconnection mode | 并离网模式：0-并网，1-离网 | Int16 | 0: Grid-tied, 1: Off-grid | / | / | / | This register will not be saved after hard reboot
53601 | 2 Bytes | RW | Energy dispatching mode | 能量调度模式：0-交流调度，1-直流调度 | Int16 | 0: AC dispatching, 1: DC dispatching | / | / | / | Making AC/DC port the controlling target, Use AC dispatching if there is no special request
53620 | 2 Bytes | RW | Reactive power control mode | 无功控制模式：0-恒PF控制，1-恒无功功率控制，2-电压/无功调节，3-PF曲线控制 | Int16 | 0: Constant PF control, 1: Constant reactive power control, 2: Volt/Var control， 3：PF Curve control(Australia) | / | / | / | Volt/Var control means reactive power will be regulated by grid voltage . PF Curve control only for Australia.
53621 | 2 Bytes | RW | PF setting | 功率因数设置（正吸收感性无功，负吸收容性无功） | Int16 | -1.00~ +1.00； +: lagging, -: leading | / | 0.01 | / | Available in AC dispatching mode(53601) and constant PF control mode(53620)
53622 | 2 Bytes | RW | Active power setting | 有功功率设置 | Int16 | ‐770.0~770.0. +: charge, power from grid to battery. -: discharge, power from battery to grid | / | 0.1 | kW | Available in AC dispatching mode(53601)
53623 | 2 Bytes | RW | Reactive power setting | 无功功率设置（正吸收感性无功，负吸收容性无功） | Int16 | ‐770.0~770.0 +: lagging, -: leading | / | 0.1 | kvar | Available in AC dispatching mode(53601) and Constant reactive power control mode(53620)
53624 | 2 Bytes | RW | Emergency power setting | 紧急功率设置 | Int16 | -1~770, +: discharge, power from battery to grid, 0:pcs turn off, -:disable | / | 1 | kW | Available in AC dispatching mode(53601). Maximum response priority.
53626 | 2 Bytes | RW | Power change mode | 功率变化模式：0-阶跃，1-斜率 | Int16 | 0: step, 1: ramp(soft-start) | / | / | /
53627 | 2 Bytes | RW | Grid recovery delay | 电网恢复延时 | Int16 | 0~600 | / | 1 | s | Keep the default value if not aware of the function of this parameter
53628 | 2 Bytes | RW | Off-grid AC voltage regulation | 离网交流电压调节 | Int16 | -0.10~0.10 | / | 0.01 | / | Available only in off-gird mode(53600). ratio * rated voltage
53631 | 2 Bytes | R/W | FVRT Limit function | 电压频率穿越限流使能 | Int16 | 0: disabled, 1: enabled | / | / | / | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53632 | 2 Bytes | RW | FVRT function | 电压频率穿越使能 | Int16 | 0: disabled, 1: enabled | / | / | / | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53633 | 2 Bytes | RW | Islanding detection enable | 孤岛检测使能 | Int16 | 0: disabled, 1: enabled | / | / | / | Keep the default value if not aware of the function of this parameter
53635 | 2 Bytes | RW | Off-grid AC voltage startup mode | 离网交流电压启动方式：0-阶跃，1-斜率 | Int16 | 0: step, 1: soft-start | / | / | / | Keep the default value if not aware of the function of this parameter
53636 | 2 Bytes | RW | Active power control mode | 有功控制模式：0-设置有功调节；1-电压自动调节；2-频率自动调节；3-电压频率自动调节； | Int16 | 0: Constant active power control。 1: Volt/Watt control。 2: Freq/Watt control。 3: Volt/Watt & Freq/Watt control | / | / | / | Volt/Watt control & Freq/Watt control means active power will be regulated by grid voltage/frequency following a curve/ramp rate ，Freq/Watt > Volt/Watt
53638 | 2 Bytes | RW | Power ramp rate | 功率变化速率 | Uint16 | USA：0.01~2.000(rated power / s) CHN：0.01~2.000(rated power / s) Australia：0.05~60.000(rated power / minuts) | / | 0.001 | / | Available in AC dispatching mode(53601) and in ramp mode(53626). If the value is 2, which means within 0.5 seconds the system can runs to full power
53639 | 2 Bytes | RW | Grid reconnection power ramp rate | 电网重连功率变化速率 | Int16 | USA：0.001~2.000(rated power / s) CHN：/ Australia：/ | / | 0.001 | rated power/s | Available in AC dispatching mode(53601) and in ramp mode(53626). Available when Grid reconnection.
53650 | 2 Bytes | RW | DC String 1: DC control mode | 直流支路1: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601)
53651 | 2 Bytes | RW | DC String 1: DC current setting | 直流支路1: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601)
53652 | 2 Bytes | RW | DC String 1: DC power setting | 直流支路1: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601)
53653 | 2 Bytes | RW | DC String 1: DC lower voltage threshold | 直流支路1: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V
53655 | 2 Bytes | RW | DC String 1: end-of-discharge voltage | 直流支路1: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V
53656 | 2 Bytes | RW | DC String 1: precharge voltage | 直流支路1: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V
53657 | 2 Bytes | RW | DC String 1: Precharge turn to fast charge judgement voltage | 直流支路1: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V
53658 | 2 Bytes | RW | DC String 1: precharge time | 直流支路1: 预充电时间 | Int16 | 0~30000 | / | 1 | min
53659 | 2 Bytes | RW | DC String 1: float charge voltage | 直流支路1: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V
53660 | 2 Bytes | RW | DC String 1: topping charge voltage | 直流支路1: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V
53661 | 2 Bytes | RW | DC String 1: topping charge turn to float charge judgement current | 直流支路1: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A
53662 | 2 Bytes | RW | DC String 1: end-of-charge current | 直流支路1: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A
53663 | 2 Bytes | RW | DC String 1: maximum charge current | 直流支路1: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A
53664 | 2 Bytes | RW | DC String 1: maximum discharge current | 直流支路1: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A
53665 | 2 Bytes | RW | DC String 1: maximum precharge current | 直流支路1: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A
53670 | 2 Bytes | RW | Over voltage region 1 protection voltage ratio | 过压保护I段电压比率 | Int16 | USA：1.05~1.25； CHN：1.05~1.35； Australia：1.05~1.20； UK：1.05~1.35； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage
53671 | 2 Bytes | RW | Over voltage region 1 protection time | 过压保护I段保护时间 | Int16 | USA：0.01~13.00； CHN：0.01~13.00； Australia：0.01~2.00； UK：0.01~13.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter
53672 | 2 Bytes | RW | Over voltage region 2 protection voltage ratio | 过压保护II段电压比率 | Int16 | USA：1.05~1.25； CHN：1.05~1.35； Australia：1.05~1.25； UK：1.05~1.35； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage
53673 | 2 Bytes | RW | Over voltage region 2 protection time | 过压保护II段保护时间 | Int16 | USA：0.01~2.00； CHN：0.01~1.00； Australia：0.01~0.50； UK：0.01~1.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter
53674 | 2 Bytes | RW | Under voltage region 1 protection voltage ratio | 欠压保护I段电压比率 | Int16 | USA：0.45~0.95； CHN：0.50~0.85； Australia：0.50~0.85； UK：0.45~0.95； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage
53675 | 2 Bytes | RW | Under voltage region 1 protection time | 欠压保护I段保护时间 | Int16 | USA：0~21.00； CHN：0.01~5.00； Australia：0~5.00； UK：0.01~5.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter
53676 | 2 Bytes | RW | Under voltage region 2 protection voltage ratio | 欠压保护II段电压比率 | Int16 | USA：0.45~0.95； CHN：0.20~0.50； Australia：/； UK：0.45~0.95； | / | 0.01 | / | invalid for Australia. ratio * rated voltage
53677 | 2 Bytes | RW | Under voltage region 2 protection time | 欠压保护II段保护时间 | Int16 | USA：0.01~11.00； CHN：0.01~1.00； Australia：/； UK：0.01~1.00； | / | 0.01 | s | invalid for Australia
53678 | 2 Bytes | RW | Under voltage region 3 protection voltage ratio | 欠压保护III段电压比率 | Int16 | USA：0.45~0.95； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA. ratio * rated voltage
53679 | 2 Bytes | RW | Under voltage region 3 protection time | 欠压保护III段保护时间 | Int16 | USA：0~1.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA
53700 | 2 Bytes | RW | Over frequency region 1 protection frequency | 过频保护I段保护频率 | Int16 | USA：0.10~4.50； CHN：0.10~3.00； Australia：0.10~3.00； UK：0.10~3.00； | / | 0.01 | Hz | Keep the default value if not aware of the function of this parameter
53701 | 2 Bytes | RW | Over frequency region 1 protection time | 过频保护I段保护时间 | Int16 | USA：0.01~300.00； CHN：0.01~300.00； Australia：0.01~5.00； UK：0.01~300.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter
53702 | 2 Bytes | RW | Over frequency region 2 protection frequency | 过频保护II段保护频率 | Int16 | USA：0.10~4.50； CHN：0.10~3.00； Australia：/； | / | 0.01 | Hz | invalid for Australia
53703 | 2 Bytes | RW | Over frequency region 2 protection time | 过频保护II段保护时间 | Int16 | USA：0.00~10.00； CHN：0.00~10.00； Australia：/； UK：0.00~10.00； | / | 0.01 | s | invalid for Australia
53704 | 2 Bytes | RW | Under frequency region 1 protection frequency | 欠频保护I段保护频率 | Int16 | USA：‐4.50~ -0.10； CHN：‐4.50~ -0.10； Australia：‐5.00~ -0.10； UK：‐4.50~ -0.10； | / | 0.01 | Hz | Keep the default value if not aware of the function of this parameter
53705 | 2 Bytes | RW | Under frequency region 1 protection time | 欠频保护I段保护时间 | Int16 | USA：0.00~600.00； CHN：0.00~600.00； Australia：0.01~5.00； UK：0.00~600.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter
53706 | 2 Bytes | RW | Under frequency region 2 protection frequency | 欠频保护II段保护频率 | Int16 | USA：‐4.50~ -0.10； CHN：‐4.50~ -0.10； Australia：/； UK：‐4.50~ -0.10； | / | 0.01 | Hz | invalid for Australia
53707 | 2 Bytes | RW | Under frequency region 2 protection time | 欠频保护II段保护时间 | Int16 | USA：0.00~10.00； CHN：0.00~10.00； Australia：/； UK：0.00~10.00； | / | 0.01 | s | invalid for Australia
53730 | 2 Bytes | RW | Over voltage region 1 ride-through voltage ratio | 过压穿越I段电压比率 | Int16 | USA：1.10~1.20； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
53731 | 2 Bytes | RW | Over voltage region 1 ride-through until | 过压穿越I段时间 | Int16 | USA：0.00~13.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53732 | 2 Bytes | RW | Over voltage region 2 ride-through voltage ratio | 过压穿越II段电压比率 | Int16 | USA：1.10~1.20； CHN：/； Australia：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
53733 | 2 Bytes | RW | Over voltage region 2 ride-through until | 过压穿越II段时间 | Int16 | USA：0.00~0.16； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53734 | 2 Bytes | RW | Under voltage region 1 ride-through voltage ratio | 欠压穿越I段电压比率 | Int16 | USA：0.50~0.88； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
53735 | 2 Bytes | RW | Under voltage region 1 ride-through until | 欠压穿越I段时间 | Int16 | USA：20.00~50.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53736 | 2 Bytes | RW | Under voltage region 2 ride-through voltage ratio | 欠压穿越II段电压比率 | Int16 | USA：0.50~0.88； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
53737 | 2 Bytes | RW | Under voltage region 2 ride-through until | 欠压穿越II段时间 | Int16 | USA：10.00~50.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53738 | 2 Bytes | RW | Under voltage region 3 ride-through voltage ratio | 欠压穿越III段电压比率 | Int16 | USA：0.40~0.50； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
53739 | 2 Bytes | RW | Under voltage region 3 ride-through until | 欠压穿越III段时间 | Int16 | USA：0.1~21.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53760 | 2 Bytes | RW | Over frequency region 1 ride-through frequency | 过频穿越I段频率 | Int16 | USA：0.1~6.00； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53761 | 2 Bytes | RW | Over frequency region 1 ride-through until | 过频穿越I段穿越时间 | Int16 | USA：20.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53762 | 2 Bytes | RW | Over frequency region 2 ride-through frequency | 过频穿越II段频率 | Int16 | USA：0.1~6.00； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53763 | 2 Bytes | RW | Over frequency region 2 ride-through until | 过频穿越II段穿越时间 | Int16 | USA：0.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53764 | 2 Bytes | RW | Under frequency region 1 ride-through frequency | 欠频穿越I段频率 | Int16 | USA：‐10~ ‐0.10； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53765 | 2 Bytes | RW | Under frequency region 1 ride-through until | 欠频穿越I段穿越时间 | Int16 | USA：20.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53766 | 2 Bytes | RW | Under frequency region 2 ride-through frequency | 欠频穿越II段频率 | Int16 | USA：‐10~ -0.10； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53767 | 2 Bytes | RW | Under frequency region 2 ride-through until | 欠频穿越II段穿越时间 | Int16 | USA：0.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
53787 | 2 Bytes | RW | Volt/Var regulation Volt point 1 | 电压无功调节点V1 | Int16 | USA：0.82~1.03； CHN：/； Australia：0.82~1.03； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53788 | 2 Bytes | RW | Volt/Var regulation Volt point 2 | 电压无功调节点V2 | Int16 | USA：0.90~1.05； CHN：/； Australia：0.90~1.05； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53789 | 2 Bytes | RW | Volt/Var regulation Volt point 3 | 电压无功调节点V3 | Int16 | USA：0.95~1.15； CHN：/； Australia：0.95~1.15； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53790 | 2 Bytes | RW | Volt/Var regulation Volt point 4 | 电压无功调节点V4 | Int16 | USA：0.97~1.18； CHN：/； Australia：0.97~1.18； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53791 | 2 Bytes | RW | Volt/Var regulation Q4 | 无功调节量Q4 | Int16 | USA：0.00~0.60； CHN：/； Australia：0.00~0.60； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53792 | 2 Bytes | RW | Volt/Var regulation Q1 | 无功调节量Q1 | Int16 | USA：0.00~0.60； CHN：/； Australia：0.00~0.60； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power, Available only when Reactive power regulation mode is set to Volt/Var(53620).
53793 | 2 Bytes | RW | Volt/Watt regulation start Volt point(High Volt) | 过压降有功起始调节点 | Int16 | USA：1.03~1.10； CHN：/； Australia：1.02~1.11； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
53796 | 2 Bytes | RW | Freq/Watt regulation start Freq point(High Freq) | 过频降有功起始调节点 | Int16 | USA：0.01~1.00； CHN：/； Australia：0.01~1.00； UK：/； | / | 0.01 | Hz | invalid for CHN. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53797 | 2 Bytes | RW | Freq/Watt regulation ramp rate | 过频降有功调节斜率 | Int16 | USA：0.02~0.07； CHN：/； Australia：/； UK：/； | / | 0.01 | Set power/Hz | only for USA; Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53820 | 2 Bytes | RW | Freq/Watt regulation end Freq point(High Freq) | 过频降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：1.00~2.00； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53821 | 2 Bytes | RW | Freq/Watt regulation start Freq point(Low Freq) | 欠频降有功起始调节点 | Int16 | USA：/； CHN：/； Australia：1.00~‐0.10； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53822 | 2 Bytes | RW | Freq/Watt regulation end Freq point(Low Freq) | 欠频降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：‐3.00~‐1.00； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53823 | 2 Bytes | RW | Over Voltage for 10 minutes | 10分钟过压幅值 | Int16 | USA：/； CHN：/； Australia：1.05~1.15； UK：/； | / | 0.01 | / | only for Australia. ratio * rated voltage
53824 | 2 Bytes | RW | PF curve regulation Power Point 1 | PF曲线模式功率调节点P1 | Int16 | USA：/； CHN：/； Australia：0.10~0.40； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53825 | 2 Bytes | RW | PF curve regulation Power Point 2 | PF曲线模式功率调节点P2 | Int16 | USA：/； CHN：/； Australia：0.40~0.60； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53826 | 2 Bytes | RW | PF curve regulation Power Point 3 | PF曲线模式功率调节点P3 | Int16 | USA：/； CHN：/； Australia：0.60~0.80； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53827 | 2 Bytes | RW | PF curve regulation Power Point 4 | PF曲线模式功率调节点P4 | Int16 | USA：/； CHN：/； Australia：0.80~1.00； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53828 | 2 Bytes | RW | PF curve regulation PF Point 1 | PF曲线模式功率因数PF1 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53829 | 2 Bytes | RW | PF curve regulation PF Point 2 | PF曲线模式功率因数PF2 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53850 | 2 Bytes | RW | PF curve regulation PF Point 3 | PF曲线模式功率因数PF3 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53851 | 2 Bytes | RW | PF curve regulation PF Point 4 | PF曲线模式功率因数PF4 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode
53852 | 2 Bytes | RW | DRMs mode enable | DRMs模式使能 | Int16 | USA：/； CHN：/； Australia：0-disable，1-enable； UK：/； | / | / | / | only for Australia.
53853 | 2 Bytes | RW | Volt/Watt regulation end Volt Point(Low Volt) | 欠压降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：0.9~1.00； UK：/； | / | 0.01 | / | only for Australia. ratio * rated voltage
53876 | 2 Bytes | RW | Volt/Var regulation Q3 | 无功调节量Q3 | Int16 | USA：0~0.6； CHN：/； Australia：0~0.6； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power. Available only when Reactive power regulation mode is set to Volt/Var(53620).
53877 | 2 Bytes | RW | Volt/Var regulation Q2 | 无功调节量Q2 | Int16 | USA：0~0.6； CHN：/； Australia：0~0.6； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power. Available only when Reactive power regulation mode is set to Volt/Var(53620).
53878 | 2 Bytes | RW | Volt/Var response time | 电压无功调节反应时间 | Int16 | USA：1~90.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when Reactive power regulation mode is set to Volt/Var(53620).
53879 | 2 Bytes | RW | Volt/Var reference voltage Vref | 电压无功调节参考电压Vref | Int16 | USA：0.95~1.05； CHN：/； Australia：/； UK：/； | / | 0.01 | V | only for USA. Available only when Reactive power regulation mode is set to Volt/Var(53620).
53880 | 2 Bytes | RW | Volt/Watt regulation end Volt point(High Volt) | 过压降有功终止调节点 | Int16 | USA：1.04~1.1； CHN：/； Australia：1.06~1.16； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
53881 | 2 Bytes | RW | Volt/Watt regulation start Power point (High Volt) | 过压降有功起始功率 | Int16 | USA：0.00~1.00； CHN：/； Australia：0.00~1.00； UK：/； | / | 0.01 | / | invalid for CHN. ratio * set power. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
53882 | 2 Bytes | RW | Volt/Watt regulation end Power point (High Volt) | 过压降有功终止功率 | Int16 | USA：0.00~1.00； CHN：/； Australia：0.00~1.00； UK：/； | / | 0.01 | / | invalid for CHN. ratio * set power. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
53883 | 2 Bytes | RW | Volt/Watt response time(High Volt) | 过压降有功反应时间 | Int16 | USA：0.5~60.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
53884 | 2 Bytes | RW | Freq/Watt response time(High Freq) | 过频降有功反应时间 | Int16 | USA：0.05~3.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode
53900 | 2 Bytes | W | System start | 系统开机 | Int16 | 1: True, else: Invalid | / | / | /
53901 | 2 Bytes | W | System stop | 系统停机 | Int16 | 1: True, else: Invalid | / | / | /
53903 | 2 Bytes | W | System Clear Fault (PCS) | 系统清除故障(PCS) | Int16 | 1: True, else: Invalid | / | / | /
56000 | 2 Bytes | W | Time Setting：year | 时间设置：年 | Uint16 | 2000~2099 | / | 1 | /
56001 | 2 Bytes | W | Time Setting：month | 时间设置：月 | Uint16 | 1~12 | / | 1 | /
56002 | 2 Bytes | W | Time Setting：day | 时间设置：日 | Uint16 | 1~31 | / | 1 | /
56003 | 2 Bytes | W | Time Setting：hour | 时间设置：小时 | Uint16 | 0~23 | / | 1 | /
56004 | 2 Bytes | W | Time Setting：minute | 时间设置：分钟 | Uint16 | 0~59 | / | 1 | /
56005 | 2 Bytes | W | Time Setting：second | 时间设置：秒 | Uint16 | 0~59 | / | 1 | /
56006 | 2 Bytes | W | BMS communication timeout setting | BMS通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the BMS communication Interruption exceeds the setting value, PCS will turn off.
56007 | 2 Bytes | W | Remote RS485 communication timeout setting | 远程485通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the RS485 communication Interruption exceeds the setting value, and PCS works in remote mode, PCS will turn off.
56008 | 2 Bytes | W | Remote TCP communication timeout setting | 远程TCP通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the TCP comm. Interruption exceeds the setting value, and PCS works in remote mode, PCS will turn off.

## MESA
MESA-PCS
Address | Address offset | Size | Access | Register Name | Type | Range | Accuracy | Unit | Comments Function Code: 0x06(W), 0x03(R) (No Offset)
0 | 1 | 32Bytes | R | model | string32 | / | / | / | Manufacturer and model number
16 | 17 | 32Bytes | R | serial | string32 | / | / | / | Serial Number
40000 | 40001 | 4Bytes | R | SunSpec_ID | uint32 | / |  |  | Well-know value. Uniquely identifies this as a SunSpec Modbus Map
40002 | 40003 | 2Bytes | R | Sunspes_DID_0001 | uint16 | / |  |  | Uniquely identifies this as a SunSpec Common Model Block
40003 | 40004 | 2Bytes | R | SunSpec_Length_0001 | uint16 | / |  |  | Length of block in 16-bit registers
40004 | 40005 | 32Bytes | R | Manufacturer | string | /
40020 | 40021 | 32Bytes | R | Model | string | / |  |  | Manufacturer specific value (32 chars)
40036 | 40037 | 16Bytes | R | Options | string | / |  |  | Manufacturer specific value (16 chars)
40044 | 40045 | 16Bytes | R | Version | string | / |  |  | Manufacturer specific value (16 chars)
40052 | 40053 | 32Bytes | R | Serial Number | string | / |  |  | Manufacturer specific value (32 chars)
40068 | 40069 | 2Bytes | RW | Device Address | uint16 | / |  |  | Modbus device address
40069 | 40070 | 2Bytes | R | Pad | Pad | / |  |  | Force event alignment
40070 | 40071 | 2Bytes | R | SunSpec_DID_0016 | uint16 |  |  |  | Include this model for a simple IPv4 network stack
40071 | 40072 | 2Bytes | R | SunSpec_Length_0016 | uint16 |  |  |  | model Length
40072 | 40073 | 8Bytes | R | Name | string |  |  |  | Interface name. (8 chars)
40076 | 40077 | 2Bytes | R | Config | uint16 |  |  |  | Force IPv4 configuration method. 0:static;1:DHCP
40077 | 40078 | 2Bytes | RW | Control | uint16 |  |  |  | Bitmask value Configure use of service;0:DNS;1:NTP
40078 | 40079 | 16Bytes | RW | Address | string |  |  |  | IP address
40086 | 40087 | 16Bytes | RW | Netmask | string |  |  |  | Netmask
40094 | 40095 | 16Bytes | RW | Gateway | string |  |  |  | Gateway IP address
40102 | 40103 | 16Bytes | RW | DNS1 | string |  |  |  | 32 bit IP address of DNS server
40110 | 40111 | 16Bytes | RW | DNS2 | string |  |  |  | 32 bit IP address of DNS server
40118 | 40119 | 8Bytes | R | MAC | uint64 |  |  |  | IEEE MAC address of this interface
40122 | 40123 | 2Bytes | RW | Link Control | uint16 |  |  |  | Bitmask value. Link control flags
40123 | 40124 | 2Bytes | R |  | pad
40124 | 40125 | 2Bytes | R | SunSpec_DID_0017 | uint16 |  |  |  | Include this model for serial interface configuration support
40125 | 40126 | 2Bytes | R | SunSpec_Length_0017 | uint16 |  |  |  | Model Length
40126 | 40127 | 8Bytes | R | Name | string |  |  |  | Interface name (8 chars)
40130 | 40131 | 4Bytes | RW | Rate | uint32 |  |  | bps | Interface baud rate in bits per second
40132 | 40133 | 2Bytes | R | Bits | uint16 |  |  |  | Number of data bits per character
40133 | 40134 | 2Bytes | R | Parity | uint16 |  |  |  | Bitmask value. Parity setting; 0:none; 1:odd; 2:even
40134 | 40135 | 2Bytes | R | Duplex | uint16 |  |  |  | 0:Full Duplex; 1:Half Duplex;
40135 | 40136 | 2Bytes | R | Flow Control | uint16 |  |  |  | 0:no flow control; 1:Hardware flow control; 2:Soft (XON/XOFF) flow control;
40136 | 40137 | 2Bytes | R | Interface Type | uint16 |  |  |  | 0:Unknow protocol; 1:RS232 interface type; 2:RS485 interface type;
40137 | 40138 | 2Bytes | R | Protocol | uint16 |  |  |  | 0:unknow protocal; 1:modbus protocal; 2:vendor specific;
40138 | 40139 | 2Bytes | R | SunSpec_DID_0103 | uint16
40139 | 40140 | 2Bytes | R | SunSpec_Length_0103 | uint16
40140 | 40141 | 2Bytes | R | A | uint16 |  |  | A | AC Current
40141 | 40142 | 2Bytes | R | AphA | uint16 |  |  | A | Phase A Current
40142 | 40143 | 2Bytes | R | AphB | uint16 |  |  | A | Phase B Currrent
40143 | 40144 | 2Bytes | R | AphC | uint16 |  |  | A | Phase C Current
40144 | 40145 | 2Bytes | R | A_SF | sunssf
40145 | 40146 | 2Bytes | R | PPVphAB | uint16 |  |  | V | Phase Voltage AB
40146 | 40147 | 2Bytes | R | PPVphBC | uint16 |  |  | V | Phase Voltage BC
40147 | 40148 | 2Bytes | R | PPVphCA | uint16 |  |  | V | Phase Voltage CA
40148 | 40149 | 2Bytes | R | PhVphA | uint16 |  |  | V | Phase Voltage AN
40149 | 40150 | 2Bytes | R | PhVphB | uint16 |  |  | V | Phase Voltage BN
40150 | 40151 | 2Bytes | R | PhVphC | uint16 |  |  | V | Phase Voltage CN
40151 | 40152 | 2Bytes | R | V_SF | sunssf
40152 | 40153 | 2Bytes | R | W | int16 |  |  | W | AC Power
40153 | 40154 | 2Bytes | R | W_SF | sunssf
40154 | 40155 | 2Bytes | R | Hz | uint16 |  |  | Hz | Line Frequency
40155 | 40156 | 2Bytes | R | Hz_SF | sunssf
40156 | 40157 | 2Bytes | R | VA | int16 |  |  | VA | AC Apparent Power
40157 | 40158 | 2Bytes | R | VA_SF | sunssf
40158 | 40159 | 2Bytes | R | VAr | int16 |  |  | VAr | AC reactive Power
40159 | 40160 | 2Bytes | R | VAr_SF | sunssf
40160 | 40161 | 2Bytes | R | PF | int16 |  |  | Pct | AC Power Factor
40161 | 40162 | 2Bytes | R | PF_SF | sunssf
40163 | 40164 | 4Bytes | R | WH | acc32 |  |  | Wh | AC Energy
40164 | 40165 | 2Bytes | R | WH_SF | sunssf
40165 | 40166 | 2Bytes | R | DCA | uint16 |  |  | A | DC Current
40166 | 40167 | 2Bytes | R | DCA_SF | sunssf
40167 | 40168 | 2Bytes | R | DCV | uint16 |  |  | V | DC Voltage
40168 | 40169 | 2Bytes | R | DCV_SF | sunssf
40169 | 40170 | 2Bytes | R | DCW | int16 |  |  | W | DC Power
40170 | 40171 | 2Bytes | R | DCW_SF | sunssf
40171 | 40172 | 2Bytes | R | TmpCab | int16 |  |  | ℃ | Cabinet Temperature
40172 | 40173 | 2Bytes | R | TmpSnk | int16 |  |  | ℃ | Heat Sink Temperature
40173 | 40174 | 2Bytes | R | TmpTrns | int16 |  |  | ℃ | Transformer Temperature
40174 | 40175 | 2Bytes | R | TmpOt | int16 |  |  | ℃ | Other Temperature
40175 | 40176 | 2Bytes | R | Tmp_SF | sunssf
40176 | 40177 | 2Bytes | R | St | uint16 |  |  |  | 1:OFF; 2:Sleeping; 3:Starting; 4:MPPT; 5:Throttled; 6:Shutting down; 7:Fault; 8:Standby; 9:Started
40177 | 40178 | 2Bytes | R | StVnd |  |  |  |  | Vendor specific operating state code
40178 | 40179 | 2Bytes | R | Evt1 |  |  |  |  | Bitmask value.Event fields. Bit0:Ground falut; Bit1:DC over voltage; Bit2:AC disconnect open; Bit3:DC disconnect open; Bit4:Grid shutdown; Bit5:Cabinet open; Bit6:Manual shutdown; Bit7:Over temperature; Bit8:Frequency above limit; Bit9:Frequency under limit; Bit10:AC Voltage above limit; Bit11:AC Voltage under limit; Bit12:Blown String fuse on input; Bit13:Under temperature; Bit14:Generic Memory or Communication error(internal); Bit15:Hardware test failure; Bit16:OTHER_ALARM; Bit17:OTHER_WARNING;
40180 | 40181 | 4Bytes | R | Evt2 |  |  |  |  | Reserved for future use
40182 | 40183 | 4Bytes | R | EvtVnd1 |  |  |  |  | Vendor defined events
40184 | 40185 | 4Bytes | R | EvtVnd2 |  |  |  |  | Vendor defined events
40186 | 40187 | 4Bytes | R | EvtVnd3 |  |  |  |  | Vendor defined events
40188 | 40189 | 4Bytes | R | EvtVnd4 |  |  |  |  | Vendor defined events
40190 | 40191 | 2Bytes | R | SunSpec_DID_64800 | uint16 |  |  |  | A well-know value 64800. Uniquely identifies this as a MESA-PCS Extensions Model
40191 | 40192 | 2Bytes | R | SunSpec_Length_64800 | uint16 |  |  |  | Well-know # of 16-bit registers to follow:8
40192 | 40193 | 2Bytes | R | LocRemCtl | uint16 |  |  |  | Inverter control mode.Enumeration. 0:Remote Control 1:Local Control
40193 | 40194 | 2Bytes | R | PCSHb | uint16 |  |  |  | Value is increment every second with periodic resets to zero.
40194 | 40195 | 2Bytes | RW | ControllerHb | uint16 |  |  |  | Value is increment every second with periodic resets to zero.
40195 | 40196 | 2Bytes | RW | PCSAlarmReset | uint16 |  |  |  | Used to reset any latched alarms. 1:Reset
40196 | 40197 | 2Bytes | RW | PCSSetOperation | uint16 |  |  |  | Commands the PCS. 1:Start the PCS 2:Stop the PCS
40197 | 40198 | 2Bytes | RW | MaxBatACha | uint16 |  |  | A | Instantaneous maxumum DC charge current.
40198 | 40199 | 2Bytes | RW | MaxBatADischa | uint16 |  |  | A | Instantaneous maxumum DC discharge current.
40199 | 40200 | 2Bytes | R | MaxBatA_SF | sunssf |  |  |  | Scale factor for instantationous DC charge/discharge current.
40200 | 40201 | 2Bytes | R | SunSpec_DID_FFFF | uint16 |  |  |  | SunSpec end Block
40201 | 40202 | 2Bytes | R | SunSpec_Length_FFFF | uint16 |  |  |  | SunsSpec of end Block

## RTC Setting (hidden)
Function Code: 0x10，start from 0xF000
Set data number | data definition | range | Comments | data quantily
1 | year | 0～99 | start from the year 2000 | 1Byte
2 | month | 1～12 |  | 1Byte
3 | day | 1～31 |  | 1Byte
4 | hour | 0～23 |  | 1Byte
5 | minute | 0～59 |  | 1Byte
6 | second | 0～59 |  | 1Byte
E.g Set System time：
Master Send：
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | data quantity | set data(1-6) | Verification
(L->H)
0x01 | 0x10 | 0xF0 | 0x00 | 0x00 | 0x03 | 0x06 | …… | CRC
Slave Reply：
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x10 | 0xF0 | 0x00 | 0x00 | 0x03 | CRC
Any abnormal，refer to Frame formats

## Version Control
版本 | 更改原因 | 更改说明 | 更改人 | 更改时间
V208 | 格式升级 | 1. 从word改为Excel，增加英文说明； 2. 光伏发电量改为4bytes； 3. 直流支路参数说明适应pv及直流源； | 任远航 | 2017-06-01
V209 | 格式升级 | 1. 03/04共用，06码支持03回读； 2. 增加HECO认证相关协议设置量； 3. 增加PCS容量、PCS初始化状态等状态量； 4. 更改光伏发电电量等； | 任远航 | 2017-09-13
V210 | 修复bug和增加需求 | 1. 直流支路启停状态定义反了； 2. 功率控制模式定义和注释调整； 3. 增对微网控制机型和同期机型增加部分协议； 4. 功率因素和无功功率的+/-分别对应感性和容性； | 任远航 | 2018-01-19
V211 | 优化和增加需求 | 加入澳洲、国内、北美三个认证协议的区别说明； 加入恒压均充、恒压浮充标志； 删除直流充放电电量； 加入无STS微网模式相关协议； 去掉STS模块的并离网状态； 增加部分R0/RW寄存器 更改部分寄存器中英文描述 | 任远航 | 2018-11-15

## (RS) (hidden)
Address | Size | Access | Register Name | Type | Comments Function Code: 0x03
53000 | 2 Bytes | R | DC-AC subsystem Fault Massage 1 | uint16
53001 | 2 Bytes | R | DC-AC subsystem Fault Massage 2 | uint16
53002 | 2 Bytes | R | DC-AC subsystem Fault Massage 3 | uint16
53003 | 2 Bytes | R | DC-AC subsystem Fault Massage 4 | uint16
53004 | 2 Bytes | R | DC-AC subsystem Fault Massage 5 | uint16
53005 | 2 Bytes | R | DC-DC subsystem Fault Massage 1 | uint16
53006 | 2 Bytes | R | DC-DC subsystem Fault Massage 2 | uint16
53007 | 2 Bytes | R | DC-DC subsystem Fault Massage 3 | uint16
53008 | 2 Bytes | R | DC-DC subsystem Fault Massage 4 | uint16
53009 | 2 Bytes | R | Monitor Fault Massage 1 | uint16
53010 | 2 Bytes | R | System State Massage 1 | uint16
53011 | 2 Bytes | R | System State Massage 2 | uint16
53012 | 2 Bytes | R | System State Massage 3 | uint16
53013 | 2 Bytes | R | System State Massage 4 | uint16
53014 | 2 Bytes | R | System State Massage 5 | uint16
53015 | 2 Bytes | R | System State Massage 6 | uint16
53016 | 2 Bytes | R | System State Massage 7 | uint16
53017 | 2 Bytes | R | System State Massage 8 | uint16
53018 | 2 Bytes | R | System State Massage 9 | uint16
53019 | 2 Bytes | R | System State Massage 10 | uint16
53020 | 2 Bytes | R | System State Massage 11 | uint16
53021 | 2 Bytes | R | System State Massage 12 | uint16
53022 | 2 Bytes | R | System State Massage 13 | uint16
53023 | 2 Bytes | R | System State Massage 14 | uint16
53024 | 2 Bytes | R | System State Massage 15 | uint16
53025 | 2 Bytes | R | System State Massage 16 | uint16
53026 | 2 Bytes | R | System State Massage 17 | uint16
53027 | 2 Bytes | R | System State Massage 18 | uint16
53028 | 2 Bytes | R | System State Massage 19 | uint16
53029 | 2 Bytes | R | System State Massage 20 | uint16
53030 | 2 Bytes | R | System State Massage 21 | uint16
53031 | 2 Bytes | R | System State Massage 22 | uint16
53032 | 2 Bytes | R | System State Massage 23 | uint16
53033 | 2 Bytes | R | System State Massage 24 | uint16
53034 | 2 Bytes | R | System State Massage 25 | uint16
53035 | 2 Bytes | R | System State Massage 26 | uint16
53036 | 2 Bytes | R | System State Massage 27 | uint16
53037 | 2 Bytes | R | System State Massage 28 | uint16
53038 | 2 Bytes | R | System State Massage 29 | uint16
53039 | 2 Bytes | R | System State Massage 30 | uint16
53040 | 2 Bytes | R | System State Massage 31 | uint16
53041 | 2 Bytes | R | System State Massage 32 | uint16
53042 | 2 Bytes | R | System State Massage 33 | uint16
53043 | 2 Bytes | R | System State Massage 34 | uint16
53044 | 2 Bytes | R | System State Massage 35 | uint16
THE FOLLOWING CONTENT ARE FOR STS
53100 | 2 Bytes | R | STS subsystem Fault Massage 1 | uint16
53101 | 2 Bytes | R | STS subsystem Fault Massage 2 | uint16
53102 | 2 Bytes | R | STS subsystem Fault Massage 3 | uint16
53103 | 2 Bytes | R | STS subsystem Fault Massage 4 | uint16
53104 | 2 Bytes | R | STS subsystem Fault Massage 5 | uint16
53105 | 2 Bytes | R | STS subsystem State Massage 1 | uint16
E.g Get PWS2 RS Data：
Master Send：
Device address | Function Code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x03 | 0xCF | 0x08 | 0x00 | 0x21 | CRC
Slave Reply：
Device address | Function Code | data quantily | data1 | … | data66 | Verification
(L->H)
0x01 | 0x03 | 0x42 | XX | …… | XX | CRC
Any abnormal，refer to Frame formats

## RO registers (hidden)
| Address | Size | Access | Register Name | 寄存器名称 | Type | Range 1.Fault: PCS shutdown 2.Alarm: PCS still work | offset | Accuracy | Unit | Comments Actual Value = Value*Accuracy + offset | PWS1 flag | PWS2 flag | PWG2 flag | multi-String flag | STS flag | Assistance Column
1 | 53000 | bit0 | RO | AC-Group: AC bus over voltage | AC模块组: 交流母线过压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
2 | 53000 | bit1 | RO | AC-Group: AC bus over frequency | AC模块组: 交流母线过频 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
3 | 53000 | bit2 | RO | AC-Group: AC bus under voltage | AC模块组: 交流母线欠压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
4 | 53000 | bit3 | RO | AC-Group: islanding protection | AC模块组: 逆变器孤岛保护 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
5 | 53000 | bit4 | RO | AC-Group: DC input over voltage | AC模块组: 直流输入过压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
6 | 53000 | bit5 | RO | AC-Group: On/Off-grid toggling error | AC模块组: 并离网切换错误 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
7 | 53000 | bit6 | RO | AC-Group: AC phase reversed | AC模块组: 交流反序 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
8 | 53000 | bit7 | RO | AC-Group: DC input under voltage | AC模块组: 直流输入欠压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
9 | 53000 | bit8 | RO | AC-Group: Overload alarm | AC模块组: 过载报警 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
10 | 53000 | bit9 | RO | AC-Group: AC bus voltage Abnormal | AC模块组: 交流母线电压异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
11 | 53000 | bit10 | RO | AC-Group: AC phase lost | AC模块组: 交流缺相 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
12 | 53000 | bit11 | RO | AC-Group: AC bus voltage asymmetric | AC模块组: 交流母线电压不平衡 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
13 | 53000 | bit12 | RO | AC-Group: AC bus under frequency | AC模块组: 交流母线欠频 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
14 | 53000 | bit13 | RO | AC-Group: Battery under energy | AC模块组: 电池电量不足 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
15 | 53000 | bit14 | RO | AC-Group: DC input over current | AC模块组: 直流输入过流 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
16 | 53000 | bit15 | RO | AC-Group: Off-grid Volt phase reversed | AC模块组: 离网电压反序 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
17 | 53001 | bit0 | RO | AC-Group: PLL fault | AC模块组: 锁相失败 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
18 | 53001 | bit1 | RO | AC-Group: Ambient over temperature | AC模块组: 环境温度过温 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
19 | 53001 | bit2 | RO | AC-Group: Ambient temp. sensor fault | AC模块组: 环温探头故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
20 | 53001 | bit3 | RO | AC-Group: Cabinet temp. sensor fault | AC模块组: 柜温探头故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
21 | 53001 | bit4 | RO | AC-Group: Cabinet over temperature | AC模块组: 机柜温度过温 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
22 | 53001 | bit5 | RO | AC-Group: Off-grid voltage phase lost | AC模块组: 离网电压缺相 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
22 | 53001 | bit6~15 | RO | reserved | / | / | / | / | / | /
23 | 53002 | bit0 | RO | AC-Group: 24V auxiliary power Fault | AC模块组: 24V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
24 | 53002 | bit1 | RO | AC-Group: emergency stopped(EPO) | AC模块组: 紧急停机 | / | 0: Normal, 1: Fault | / | / | / | EPO button pressed | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
25 | 53002 | bit2 | RO | AC-Group: Grounding fault | AC模块组: 接地故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
26 | 53002 | bit3 | RO | AC-Group: DC bus over voltage | AC模块组: 直流母线过压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
27 | 53002 | bit4 | RO | AC-Group: Module over temperature | AC模块组: 模块温度过温 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
28 | 53002 | bit5 | RO | AC-Group: Module current asymmetric | AC模块组: 模块电流不平衡 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
29 | 53002 | bit6 | RO | AC-Group: Fan Fault | AC模块组: 风扇故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
30 | 53002 | bit7 | RO | AC-Group: DC relay open circuit | AC模块组: 直流继电器开路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
31 | 53002 | bit8 | RO | AC-Group: Calibration parameter Abnormal | AC模块组: 校准参数异常 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
32 | 53002 | bit9 | RO | AC-Group: Bus voltage unbalanced | AC模块组: 母线电压不平衡 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
33 | 53002 | bit10 | RO | AC-Group: Fuse blown | AC模块组: 保险故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
34 | 53002 | bit11 | RO | AC-Group: DSP initializing fault | AC模块组: DSP初始化故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
35 | 53002 | bit12 | RO | AC-Group: DC soft start failed | AC模块组: 直流软启动失败 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
36 | 53002 | bit13 | RO | AC-Group: CAN A comm. Fault | AC模块组: CANA通讯故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
37 | 53002 | bit14 | RO | AC-Group: DC input reversed | AC模块组: 直流输入反接 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
38 | 53002 | bit15 | RO | AC-Group: AC current DC component Abnormal | AC模块组: 交流电流直流分量异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
39 | 53003 | bit0 | RO | AC-Group: Transformer over temp. | AC模块组: 变压器过温 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
40 | 53003 | bit1 | RO | AC-Group: U2 comm. 2 Abnormal | AC模块组: U2通信异常2 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
41 | 53003 | bit2 | RO | AC-Group: Tripped by BMS or DC switch | AC模块组: BMS故障或直流开关断开 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
42 | 53003 | bit3 | RO | AC-Group: SPD fault | AC模块组: 防雷器故障 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
43 | 53003 | bit4 | RO | AC-Group: Overload timeout fault | AC模块组: 过载超时故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
44 | 53003 | bit5 | RO | AC-Group: AC soft start failed | AC模块组: 交流软启动失败 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
45 | 53003 | bit6 | RO | AC-Group: Synchronous signal 1 fault | AC模块组: 同步信号故障1 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
46 | 53003 | bit7 | RO | AC-Group: DSP version fault | AC模块组: DSP版本故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
47 | 53003 | bit8 | RO | AC-Group: AC relay open circuit | AC模块组: 交流继电器开路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
48 | 53003 | bit9 | RO | AC-Group: Sampling zero Abnormal | AC模块组: 采样零点异常 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
49 | 53003 | bit10 | RO | AC-Group: U2 comm. 1 Abnormal | AC模块组: U2通信异常1 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
50 | 53003 | bit11 | RO | AC-Group: 15V auxiliary power Fault | AC模块组: 15V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
51 | 53003 | bit12 | RO | AC-Group: Module ID reduplicated | AC模块组: 模块重号故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
52 | 53003 | bit13 | RO | AC-Group: RS485 comm. Fault | AC模块组: RS485通讯故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
53 | 53003 | bit14 | RO | AC-Group: CAN B comm. Fault | AC模块组: CANB通讯故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
54 | 53003 | bit15 | RO | AC-Group: Restart too much | AC模块组: 重启过多 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
55 | 53004 | bit0 | RO | AC-Group: CPLD version Fault | AC模块组: CPLD版本故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
56 | 53004 | bit1 | RO | AC-Group: Hardware version Fault | AC模块组: 硬件版本故障 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
57 | 53004 | bit2 | RO | AC-Group: DC relay short circuit | AC模块组: 直流继电器短路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
58 | 53004 | bit3 | RO | AC-Group: DC bus under voltage | AC模块组: 直流母线欠压 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
59 | 53004 | bit4 | RO | AC-Group: AC relay short circuit | AC模块组: 交流继电器短路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
60 | 53004 | bit5 | RO | AC-Group: Synchronous signal 2 fault | AC模块组: 同步信号故障2 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
61 | 53004 | bit6 | RO | AC-Group: Parameter mismatch | AC模块组: 参数不匹配 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
62 | 53004 | bit7 | RO | AC-Group: CAN C comm. Fault | AC模块组: CANC通讯故障 | / | 0: Normal, 1: Alarm | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
63 | 53004 | bit8 | RO | AC-Group: Ambient humidity too high | AC模块组: 环境湿度过高 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
64 | 53004 | bit9 | RO | AC-Group: BMS voltage Abnormal | AC模块组: BMS电压异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
65 | 53004 | bit10 | RO | AC-Group: BMS current Abnormal | AC模块组: BMS电流异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
66 | 53004 | bit11 | RO | AC-Group: BMS temperature Abnormal | AC模块组: BMS温度异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
67 | 53004 | bit12 | RO | AC-Group: BMS shutdown | AC模块组: BMS跳机 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
68 | 53004 | bit13 | RO | AC-Group: Insulation detection Abnormal | AC模块组: 绝缘检测异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
69 | 53004 | bit14 | RO | AC-Group: Hardware sampling Abnormal | AC模块组: 硬件采样异常 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
69 | 53004 | bit15 | RO | reserved | / | / | / | / | / | /
69 | 53005 | bit0 | RO | DC-Group: DC bus over voltage | DC模块组: 直流母线过压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit1 | RO | DC-Group: DC bus under voltage | DC模块组: 直流母线欠压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit2 | RO | DC-Group: DC input over voltage | DC模块组: 直流输入过压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit3 | RO | DC-Group: DC input under voltage | DC模块组: 直流输入欠压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit4 | RO | DC-Group: DC input over current | DC模块组: 直流输入过流 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit5 | RO | DC-Group: DC input power down | DC模块组: 直流输入掉电 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit6 | RO | DC-Group: Restart too much | DC模块组: 重启过多 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit7 | RO | DC-Group: Battery relay short circuit | DC模块组: 电池继电器短路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit8 | RO | DC-Group: PV under energy | DC模块组: 光伏能量不足 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit9 | RO | DC-Group: Battery under energy | DC模块组: 电池电量不足 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit10 | RO | reserved | / | / | / | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit11 | RO | DC-Group: Tripped by BMS or DC switch | DC模块组: BMS故障或直流开关断开 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit12 | RO | DC-Group: U2 comm. 1 Abnormal | DC模块组: U2通信异常1 | / | 0: Normal, 1: Alarm | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53005 | bit13~15 | RO | reserved |  | / |  | / | / | /
69 | 53006 | bit0~15 | RO | reserved |  | / |  | / | / | /
69 | 53007 | bit0 | RO | DC-Group: Module current asymmetric | DC模块组: 模块电流不平衡 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit1 | RO | 预留 | 预留 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series
69 | 53007 | bit2 | RO | DC-Group: 24V auxiliary power Fault | DC模块组: 24V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit3 | RO | DC-Group: emergent stopped(EPO) | DC模块组: 紧急停机 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit4 | RO | DC-Group: Grounding fault | DC模块组: 接地故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit5 | RO | DC-Group: Bus voltage unbalanced | DC模块组: 母线电压不平衡 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit6 | RO | DC-Group: Module over temperature | DC模块组: 模块温度过温 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit7 | RO | DC-Group: Fan Fault | DC模块组: 风扇故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit8 | RO | DC-Group: Battery relay open circuit | DC模块组: 电池继电器开路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit9 | RO | DC-Group: Calibration parameter Abnormal | DC模块组: 校准参数异常 | / | 0: Normal, 1: Alarm | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit10 | RO | DC-Group: Fuse blown | DC模块组: 保险故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit11 | RO | DC-Group: DSP initializing fault | DC模块组: DSP初始化故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit12 | RO | DC-Group: Battery soft start failed | DC模块组: 电池软启动失败 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit13 | RO | DC-Group: CAN A comm. Fault | DC模块组: CANA通讯故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit14 | RO | DC-Group: Bus relay open circuit | DC模块组: 母线继电器开路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53007 | bit15 | RO | DC-Group: Bus soft start failed | DC模块组: 母线软启动失败 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit0 | RO | DC-Group: DSP verision Fault | DC模块组: DSP版本故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit1 | RO | DC-Group: CPLD version Fault | DC模块组: CPLD版本故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit2 | RO | DC-Group: Parameter mismatch | DC模块组: 参数不匹配 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit3 | RO | DC-Group: Hardware version fault | DC模块组: 硬件版本故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit4 | RO | DC-Group: RS485 communication Fault | DC模块组: 485通讯故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit5 | RO | DC-Group: CAN B comm. Fault | DC模块组: CANB通讯故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit6 | RO | DC-Group: Module ID reduplicated | DC模块组: 模块重号故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit7 | RO | 预留 | 预留 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series
69 | 53008 | bit8 | RO | DC-Group: 15V auxiliary power Fault | DC模块组: 15V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit9 | RO | DC-Group: Bus relay short circuit | DC模块组: 母线继电器短路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit10 | RO | DC-Group: BMS voltage Abnormal | DC模块组: BMS电压异常 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit11 | RO | DC-Group: BMS current Abnormal | DC模块组: BMS电流异常 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit12 | RO | DC-Group: BMS temperature Abnormal | DC模块组: BMS温度异常 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit13 | RO | DC-Group: BMS shutdown | DC模块组: BMS跳机 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit14 | RO | DC-Group: Insulation detection Abnormal | DC模块组: 绝缘检测异常 | / | 0: Normal, 1: Fault | / | / | / | Only for PWS2 or PWG2 series |  | PWS2 | PWG2 |  |  | PWS2PWG2
69 | 53008 | bit15 | RO | reserved | / | / | / | / | / | /
69 | 53009 | bit0 | RO | PCS: Pv under voltage | PCS: 光伏欠压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWG2 series |  |  | PWG2 |  |  | PWG2
69 | 53009 | bit1 | RO | PCS: Pv over voltage | PCS: 光伏过压 | / | 0: Normal, 1: Fault | / | / | / | Only for PWG2 series |  |  | PWG2 |  |  | PWG2
69 | 53009 | bit2 | RO | PCS: Pv contactor short circuit | PCS: 光伏接触器短路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWG2 series |  |  | PWG2 |  |  | PWG2
69 | 53009 | bit3 | RO | PCS: Pv contactor open circuit | PCS: 光伏接触器开路 | / | 0: Normal, 1: Fault | / | / | / | Only for PWG2 series |  |  | PWG2 |  |  | PWG2
70 | 53009 | bit4 | RO | PCS: PE-N contactor short circuit | PCS: PE-N接触器短路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
71 | 53009 | bit5 | RO | PCS: PE-N contactor open circuit | PCS: PE-N接触器开路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
72 | 53009 | bit6 | RO | PCS: Neutral contactor short circuit | PCS: N接触器短路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
73 | 53009 | bit7 | RO | PCS: Neutral contactor open circuit | PCS: N接触器开路 | / | 0: Normal, 1: Fault | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
73 | 53009 | bit8~15 | RO | reserved | / | / | / | / | / | /
74 | 53010 | bit0 | RO | AC-Group: On/Off status | AC模块组: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
75 | 53010 | bit1 | RO | Standby status | 待机状态 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
76 | 53010 | bit2 | RO | Grid-tied status | 并网状态 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
77 | 53010 | bit3 | RO | Off-grid status | 离网状态 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
77 | 53010 | bit4~7 | RO | reserved | / | / | / | / | / | /
78 | 53010 | bit8 | RO | Local manual control | 本地手动控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS will NOT respond to remote controlling | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
79 | 53010 | bit9 | RO | Local auto control | 本地自动控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS will NOT respond to remote controlling | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
80 | 53010 | bit10 | RO | Remote control | 远程控制状态 | / | 0: False, 1: True | / | / | / | In this mode, PCS Will respond to remote controlling | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
80 | 53010 | bit11~15 | RO | reserved | / | / | / | / | / | /
81 | 53011 | bit0 | RO | AC dispatch mode enabled | 交流调度模式使能 | / | 0: False, 1: True | / | / | / | Making AC port the controlling target | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
82 | 53011 | bit1 | RO | DC dispatch mode enabled | 直流调度模式使能 | / | 0: False, 1: True | / | / | / | Making DC port the controlling target | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
83 | 53011 | bit2 | RO | FVRT enabled | 穿越使能 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
84 | 53011 | bit3 | RO | Island detection enable | 孤岛检测使能 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
84 | 53011 | bit4 | RO | Drooping status | 下垂状态 | / | 0: False, 1: True | / | / | / | 仅用于并离网切换控制
84 | 53011 | bit5 | RO | Quasi-synch status | 准同期状态 | / | 0: False, 1: True | / | / | / | 仅用于并离网切换控制
84 | 53011 | bit6~7 | RO | reserved | / | / | / | / | / | /
85 | 53011 | bit8 | RO | Ac switch closed | 交流开关闭合 | / | 0: Open, 1: Closed | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
86 | 53011 | bit9 | RO | Alrm status | 告警状态 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
87 | 53011 | bit10 | RO | Fault status | 故障状态 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
87 | 53011 | bit11 | RO | PV Bus switch status | PV母线开关状态 | / | 0: Open, 1: Closed | / | / | / | Only for PWG2 series |  |  | PWG2 |  |  | PWG2
88 | 53011 | bit12 | RO | PCS initialization status | PCS初始化状态 | / | 0: Unfinished, 1: Finished | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
88 | 53011 | bit13~15 | RO | reserved | / | / | / | / | / | /
88 | 53012 | bit0~15 | RO | reserved | / | / | / | / | / | /
89 | 53013 | bit0 | RO | DC String 1: battery fully charged | 直流支路1: 电池充满 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
90 | 53013 | bit1 | RO | DC String 1: battery totally discharged | 直流支路1: 电池放空 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
91 | 53013 | bit2 | RO | DC String 1: charging | 直流支路1: 充电 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
92 | 53013 | bit3 | RO | DC String 1: discharging | 直流支路1: 放电 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
93 | 53013 | bit4 | RO | DC String 1: PV generating | 直流支路1: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types | PWS1 | PWS2 |  |  |  | PWS1PWS2
94 | 53013 | bit5 | RO | DC String 1: PV sleeping | 直流支路1: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types | PWS1 | PWS2 |  |  |  | PWS1PWS2
95 | 53013 | bit6 | RO | DC String 1: battery constant voltage topping charging | 直流支路1: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
96 | 53013 | bit7 | RO | DC String 1: battery constant voltage float charging | 直流支路1: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
97 | 53013 | bit8 | RO | DC String 1: DC switch status | 直流支路1: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
98 | 53013 | bit9 | RO | DC String 1: PV MPPT | 直流支路1: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types | PWS1 | PWS2 |  |  |  | PWS1PWS2
99 | 53013 | bit10~12 | RO | DC String 1: Insulation detection status | 直流支路1: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
99 | 53013 | bit13~15 | RO | reserved | / | / | / | / | / | /
100 | 53014 | bit0 | RO | DC String 1: On/Off status | 直流支路1: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
100 | 53014 | bit1 | RO | reserved | 直流支路1: 待机状态 | / | / | / | / | / | Disabled，不开放
100 | 53014 | bit2~15 | RO | reserved | / | / | / | / | / | /
100 | 53015 | bit0~15 | RO | reserved | / | / | / | / | / | / | /
100 | 53016 | bit0 | RO | DC String 2: battery fully charged | 直流支路2: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit1 | RO | DC String 2: battery totally discharged | 直流支路2: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit2 | RO | DC String 2: charging | 直流支路2: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit3 | RO | DC String 2: discharging | 直流支路2: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit4 | RO | DC String 2: PV generating | 直流支路2: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit5 | RO | DC String 2: PV sleeping | 直流支路2: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit6 | RO | DC String 2: battery constant voltage topping charging | 直流支路2: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit7 | RO | DC String 2: battery constant voltage float charging | 直流支路2: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit8 | RO | DC String 2: DC switch status | 直流支路2: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit9 | RO | DC String 2: PV MPPT | 直流支路2: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit10~12 | RO | DC String 2: Insulation detection status | 直流支路2: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
100 | 53016 | bit13~15 | RO | reserved | / | / | / | / | / | /
100 | 53017 | bit0 | RO | DC String 2: On/Off status | 直流支路2: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53017 | bit1 | RO | reserved | 直流支路2: 待机状态 | / | / | / | / | / | Disabled，不开放
100 | 53017 | bit2~15 | RO | reserved | / | / | / | / | / | /
100 | 53018 | bit0~15 | RO | reserved | / | / | / | / | / | /
100 | 53019 | bit0 | RO | DC String 3: battery fully charged | 直流支路3: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit1 | RO | DC String 3: battery totally discharged | 直流支路3: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit2 | RO | DC String 3: charging | 直流支路3: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit3 | RO | DC String 3: discharging | 直流支路3: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit4 | RO | DC String 3: PV generating | 直流支路3: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit5 | RO | DC String 3: PV sleeping | 直流支路3: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit6 | RO | DC String 3: battery constant voltage topping charging | 直流支路3: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit7 | RO | DC String 3: battery constant voltage float charging | 直流支路3: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit8 | RO | DC String 3: DC switch status | 直流支路3: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit9 | RO | DC String 3: PV MPPT | 直流支路3: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit10~12 | RO | DC String 3: Insulation detection status | 直流支路3: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
100 | 53019 | bit13~15 | RO | reserved | / | / | / | / | / | /
100 | 53020 | bit0 | RO | DC String 3: On/Off status | 直流支路3: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53020 | bit1 | RO | reserved | 直流支路3: 待机状态 | / | / | / | / | / | Disabled，不开放
100 | 53020 | bit2~15 | RO | reserved | / | / | / | / | / | /
100 | 53021 | bit0~15 | RO | reserved | / | / | / | / | / | /
100 | 53022 | bit0 | RO | DC String 4: battery fully charged | 直流支路4: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit1 | RO | DC String 4: battery totally discharged | 直流支路4: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit2 | RO | DC String 4: charging | 直流支路4: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit3 | RO | DC String 4: discharging | 直流支路4: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit4 | RO | DC String 4: PV generating | 直流支路4: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit5 | RO | DC String 4: PV sleeping | 直流支路4: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit6 | RO | DC String 4: battery constant voltage topping charging | 直流支路4: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit7 | RO | DC String 4: battery constant voltage float charging | 直流支路4: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit8 | RO | DC String 4: DC switch status | 直流支路4: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit9 | RO | DC String 4: PV MPPT | 直流支路4: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit10~12 | RO | DC String 4: Insulation detection status | 直流支路4: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
100 | 53022 | bit13~15 | RO | reserved | / | / | / | / | / | /
100 | 53023 | bit0 | RO | DC String 4: On/Off status | 直流支路4: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
100 | 53023 | bit1 | RO | reserved | 直流支路4: 待机状态 | / | / | / | / | / | Disabled，不开放
100 | 53023 | bit2~15 | RO | reserved | / | / | / | / | / | /
100 | 53024 | bit0~15 | RO | reserved | / | / | / | / | / | /
101 | 53025 | bit0 | RO | AC-Group: module 1 online | AC模块组: 模块1在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
102 | 53025 | bit1 | RO | AC-Group: module 2 online | AC模块组: 模块2在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
103 | 53025 | bit2 | RO | AC-Group: module 3 online | AC模块组: 模块3在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
104 | 53025 | bit3 | RO | AC-Group: module 4 online | AC模块组: 模块4在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
105 | 53025 | bit4 | RO | AC-Group: module 5 online | AC模块组: 模块5在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
106 | 53025 | bit5 | RO | AC-Group: module 6 online | AC模块组: 模块6在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
107 | 53025 | bit6 | RO | AC-Group: module 7 online | AC模块组: 模块7在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
108 | 53025 | bit7 | RO | AC-Group: module 8 online | AC模块组: 模块8在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
109 | 53025 | bit8 | RO | AC-Group: module 9 online | AC模块组: 模块9在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
110 | 53025 | bit9 | RO | AC-Group: module 10 online | AC模块组: 模块10在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
111 | 53025 | bit10 | RO | Rack Func board online | 机架功能板在线 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
111 | 53025 | bit11~15 | RO | reserved | / | / | / | / | / | /
111 | 53026 | bit0 | RO | DC-Group: module 1 online | DC模块组: 模块1在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit1 | RO | DC-Group: module 2 online | DC模块组: 模块2在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit2 | RO | DC-Group: module 3 online | DC模块组: 模块3在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit3 | RO | DC-Group: module 4 online | DC模块组: 模块4在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit4 | RO | DC-Group: module 5 online | DC模块组: 模块5在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit5 | RO | DC-Group: module 6 online | DC模块组: 模块6在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit6 | RO | DC-Group: module 7 online | DC模块组: 模块7在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit7 | RO | DC-Group: module 8 online | DC模块组: 模块8在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit8 | RO | DC-Group: module 9 online | DC模块组: 模块9在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit9 | RO | DC-Group: module 10 online | DC模块组: 模块10在线 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
111 | 53026 | bit10~15 | RO | reserved | / | / | / | / | / | /
112 | 53027 | bit0 | RO | AC-Group: module 1 running | AC模块组: 模块1运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
113 | 53027 | bit1 | RO | AC-Group: module 2 running | AC模块组: 模块2运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
114 | 53027 | bit2 | RO | AC-Group: module 3 running | AC模块组: 模块3运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
115 | 53027 | bit3 | RO | AC-Group: module 4 running | AC模块组: 模块4运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
116 | 53027 | bit4 | RO | AC-Group: module 5 running | AC模块组: 模块5运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
117 | 53027 | bit5 | RO | AC-Group: module 6 running | AC模块组: 模块6运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
118 | 53027 | bit6 | RO | AC-Group: module 7 running | AC模块组: 模块7运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
119 | 53027 | bit7 | RO | AC-Group: module 8 running | AC模块组: 模块8运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
120 | 53027 | bit8 | RO | AC-Group: module 9 running | AC模块组: 模块9运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
121 | 53027 | bit9 | RO | AC-Group: module 10 running | AC模块组: 模块10运行 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
121 | 53027 | bit10~15 | RO | reserved | / | / | / | / | / | /
121 | 53028 | bit0 | RO | DC-Group: module 1 running | DC模块组: 模块1运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit1 | RO | DC-Group: module 2 running | DC模块组: 模块2运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit2 | RO | DC-Group: module 3 running | DC模块组: 模块3运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit3 | RO | DC-Group: module 4 running | DC模块组: 模块4运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit4 | RO | DC-Group: module 5 running | DC模块组: 模块5运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit5 | RO | DC-Group: module 6 running | DC子系统模块6运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit6 | RO | DC-Group: module 7 running | DC子系统模块7运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit7 | RO | DC-Group: module 8 running | DC模块组: 模块8运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit8 | RO | DC-Group: module 9 running | DC模块组: 模块9运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit9 | RO | DC-Group: module 10 running | DC模块组: 模块10运行 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
121 | 53028 | bit10~15 | RO | reserved | / | / | / | / | / | /
122 | 53029 | bit0 | RO | AC-Group: module 1 Alarm | AC模块组: 模块1告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
123 | 53029 | bit1 | RO | AC-Group: module 2 Alarm | AC模块组: 模块2告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
124 | 53029 | bit2 | RO | AC-Group: module 3 Alarm | AC模块组: 模块3告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
125 | 53029 | bit3 | RO | AC-Group: module 4 Alarm | AC模块组: 模块4告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
126 | 53029 | bit4 | RO | AC-Group: module 5 Alarm | AC模块组: 模块5告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
127 | 53029 | bit5 | RO | AC-Group: module 6 Alarm | AC模块组: 模块6告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
128 | 53029 | bit6 | RO | AC-Group: module 7 Alarm | AC模块组: 模块7告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
129 | 53029 | bit7 | RO | AC-Group: module 8 Alarm | AC模块组: 模块8告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
130 | 53029 | bit8 | RO | AC-Group: module 9 Alarm | AC模块组: 模块9告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
131 | 53029 | bit9 | RO | AC-Group: module 10 Alarm | AC模块组: 模块10告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
132 | 53029 | bit10 | RO | Rack Func board Alarm | 机架功能板告警 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
132 | 53029 | bit11~15 | RO | reserved | / | / | / | / | / | /
132 | 53030 | bit0 | RO | DC-Group: module 1 Alarm | DC模块组: 模块1告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit1 | RO | DC-Group: module 2 Alarm | DC模块组: 模块2告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit2 | RO | DC-Group: module 3 Alarm | DC模块组: 模块3告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit3 | RO | DC-Group: module 4 Alarm | DC模块组: 模块4告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit4 | RO | DC-Group: module 5 Alarm | DC模块组: 模块5告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit5 | RO | DC-Group: module 6 Alarm | DC模块组: 模块6告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit6 | RO | DC-Group: module 7 Alarm | DC模块组: 模块7告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit7 | RO | DC-Group: module 8 Alarm | DC模块组: 模块8告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit8 | RO | DC-Group: module 9 Alarm | DC模块组: 模块9告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit9 | RO | DC-Group: module 10 Alarm | DC模块组: 模块10告警 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
132 | 53030 | bit10~15 | RO | reserved | / | / | / | / | / | /
133 | 53031 | bit0 | RO | AC-Group: module 1 fault | AC模块组: 模块1故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
134 | 53031 | bit1 | RO | AC-Group: module 2 fault | AC模块组: 模块2故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
135 | 53031 | bit2 | RO | AC-Group: module 3 fault | AC模块组: 模块3故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
136 | 53031 | bit3 | RO | AC-Group: module 4 fault | AC模块组: 模块4故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
137 | 53031 | bit4 | RO | AC-Group: module 5 fault | AC模块组: 模块5故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
138 | 53031 | bit5 | RO | AC-Group: module 6 fault | AC模块组: 模块6故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
139 | 53031 | bit6 | RO | AC-Group: module 7 fault | AC模块组: 模块7故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
140 | 53031 | bit7 | RO | AC-Group: module 8 fault | AC模块组: 模块8故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
141 | 53031 | bit8 | RO | AC-Group: module 9 fault | AC模块组: 模块9故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
142 | 53031 | bit9 | RO | AC-Group: module 10 fault | AC模块组: 模块10故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
143 | 53031 | bit10 | RO | Rack Func board fault | 机架功能板故障 | / | 0: False, 1: True | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
143 | 53031 | bit11~15 | RO | reserved | / | / | / | / | / | /
143 | 53032 | bit0 | RO | DC-Group: module 1 fault | DC模块组: 模块1故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit1 | RO | DC-Group: module 2 fault | DC模块组: 模块2故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit2 | RO | DC-Group: module 3 fault | DC模块组: 模块3故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit3 | RO | DC-Group: module 4 fault | DC模块组: 模块4故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit4 | RO | DC-Group: module 5 fault | DC模块组: 模块5故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit5 | RO | DC-Group: module 6 fault | DC模块组: 模块6故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit6 | RO | DC-Group: module 7 fault | DC模块组: 模块7故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit7 | RO | DC-Group: module 8 fault | DC模块组: 模块8故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit8 | RO | DC-Group: module 9 fault | DC模块组: 模块9故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit9 | RO | DC-Group: module 10 fault | DC模块组: 模块10故障 | / | 0: False, 1: True | / | / | / |  |  | PWS2 | PWG2 |  |  | PWS2PWG2
143 | 53032 | bit10~15 | RO | reserved | / | / | / | / | / | /
143 | 53033 | bit0 | RO | DC String 5: battery fully charged | 直流支路5: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit1 | RO | DC String 5: battery totally discharged | 直流支路5: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit2 | RO | DC String 5: charging | 直流支路5: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit3 | RO | DC String 5: discharging | 直流支路5: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit4 | RO | DC String 5: PV generating | 直流支路5: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit5 | RO | DC String 5: PV sleeping | 直流支路5: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit6 | RO | DC String 5: battery constant voltage topping charging | 直流支路5: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit7 | RO | DC String 5: battery constant voltage float charging | 直流支路5: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit8 | RO | DC String 5: DC switch status | 直流支路5: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit9 | RO | DC String 5: PV MPPT | 直流支路5: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit10~12 | RO | DC String 5: Insulation detection status | 直流支路5: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
143 | 53033 | bit13~15 | RO | reserved | / | / | / | / | / | /
143 | 53034 | bit0 | RO | DC String 5: On/Off status | 直流支路5: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53034 | bit1 | RO | reserved | 直流支路5: 待机状态 | / |  | / | / | / | Disabled，不开放
143 | 53034 | bit2~15 | RO | reserved | / | / | / | / | / | /
143 | 53035 | bit0~15 | RO | reserved | / | / | / | / | / | /
143 | 53036 | bit0 | RO | DC String 6: battery fully charged | 直流支路6: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit1 | RO | DC String 6: battery totally discharged | 直流支路6: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit2 | RO | DC String 6: charging | 直流支路6: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit3 | RO | DC String 6: discharging | 直流支路6: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit4 | RO | DC String 6: PV generating | 直流支路6: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit5 | RO | DC String 6: PV sleeping | 直流支路6: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit6 | RO | DC String 6: battery constant voltage topping charging | 直流支路6: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit7 | RO | DC String 6: battery constant voltage float charging | 直流支路6: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit8 | RO | DC String 6: DC switch status | 直流支路6: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit9 | RO | DC String 6: PV MPPT | 直流支路6: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit10~12 | RO | DC String 6: Insulation detection status | 直流支路6: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
143 | 53036 | bit13~15 | RO | reserved | / | / | / | / | / | /
143 | 53037 | bit0 | RO | DC String 6: On/Off status | 直流支路6: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53037 | bit1 | RO | reserved | 直流支路6: 待机状态 | / | / | / | / | / | Disabled，不开放
143 | 53037 | bit2~15 | RO | reserved | / | / | / | / | / | /
143 | 53038 | bit0~15 | RO | reserved | / | / | / | / | / | /
143 | 53039 | bit0 | RO | DC String 7: battery fully charged | 直流支路7: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit1 | RO | DC String 7: battery totally discharged | 直流支路7: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit2 | RO | DC String 7: charging | 直流支路7: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit3 | RO | DC String 7: discharging | 直流支路7: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit4 | RO | DC String 7: PV generating | 直流支路7: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit5 | RO | DC String 7: PV sleeping | 直流支路7: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit6 | RO | DC String 7: battery constant voltage topping charging | 直流支路7: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit7 | RO | DC String 7: battery constant voltage float charging | 直流支路7: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit8 | RO | DC String 7: DC switch status | 直流支路7: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit9 | RO | DC String 7: PV MPPT | 直流支路7: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit10~12 | RO | DC String 7: Insulation detection status | 直流支路7: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
143 | 53039 | bit13~15 | RO | reserved | / | / | / | / | / | /
143 | 53040 | bit0 | RO | DC String 7: On/Off status | 直流支路7: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53040 | bit1 | RO | reserved | 直流支路7: 待机状态 | / | / | / | / | / | Disabled，不开放
143 | 53040 | bit2~15 | RO | reserved | / | / | / | / | / | /
143 | 53041 | bit0~15 | RO | reserved | / | / | / | / | / | /
143 | 53042 | bit0 | RO | DC String 8: battery fully charged | 直流支路8: 电池充满 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit1 | RO | DC String 8: battery totally discharged | 直流支路8: 电池放空 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit2 | RO | DC String 8: charging | 直流支路8: 充电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit3 | RO | DC String 8: discharging | 直流支路8: 放电 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit4 | RO | DC String 8: PV generating | 直流支路8: 光伏发电 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit5 | RO | DC String 8: PV sleeping | 直流支路8: 光伏休眠 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit6 | RO | DC String 8: battery constant voltage topping charging | 直流支路8: 电池恒压均充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit7 | RO | DC String 8: battery constant voltage float charging | 直流支路8: 电池恒压浮充 | / | 0: False, 1: True | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit8 | RO | DC String 8: DC switch status | 直流支路8: 直流开关状态 | / | 0: Open, 1: Closed | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit9 | RO | DC String 8: PV MPPT | 直流支路8: 光伏MPPT状态 | / | 0: False, 1: True | / | / | / | Only for PWS2 PV input types |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit10~12 | RO | DC String 8: Insulation detection status | 直流支路8: 绝缘检测状态 | / | 0-无效，1-待检测，2-检测中，3-检测完成，4-检测失败； | / | / | / | 无绝缘检测选件-0；直流电压无-1；直流电压从无到有且无开机命令-2；检测完毕-3；检测出故障或检测被中断判断-4； |  |  |  | Multi-String |  | Multi-String
143 | 53042 | bit13~15 | RO | reserved | / | / | / | / | / | /
143 | 53043 | bit0 | RO | DC String 8: On/Off status | 直流支路8: 启停状态 | / | 0: Stop, 1: Running | / | / | / |  |  |  |  | Multi-String |  | Multi-String
143 | 53043 | bit1 | RO | reserved | 直流支路8: 待机状态 | / | / | / | / | / | Disabled，不开放
143 | 53043 | bit2~15 | RO | reserved | / | / | / | / | / | /
143 | 53044~53099 | / | RO | reserved | / | / | / | / | / | /
143 | 53100 | bit0 | RO | STS: grid voltage reversed | STS: 电网电压反序 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit1 | RO | STS: grid AC voltage phase lost | STS: 电网电压缺相 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit2 | RO | STS: off-grid AC voltage reversed | STS: 离网电压反序 | / | 0: Normal, 1: Fault | / | / | / | Abnromal means the external cause caused the switch failed, |  |  |  |  | STS | STS
143 | 53100 | bit3 | RO | STS: off-grid AC voltage phase lost | STS: 离网电压缺相 | / | 0: Normal, 1: Fault | / | / | / | Fault means the internal cause caused the switch failed, |  |  |  |  | STS | STS
143 | 53100 | bit4 | RO | STS: Calibration parameter abnormal | STS: 校准参数异常 | / | 0: Normal, 1: Alarm | / | / | / | Alarm means switch is normal |  |  |  |  | STS | STS
143 | 53100 | bit5 | RO | STS: Sampling zero abnormal | STS: 采样零点异常 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit6 | RO | STS: Overload alarm | STS: 过载报警 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit7 | RO | STS: Ambient over temperature | STS: 环境温度过温 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit8 | RO | STS: PLL fault | STS: 锁相失败 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit9 | RO | STS: Grid voltage asymmetric | STS: 电网电压不平衡 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit10 | RO | STS: Grid under voltage | STS: 电网侧欠压 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit11 | RO | STS: Grid over voltage | STS: 电网侧过压 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit12 | RO | STS: Grid under frequency | STS: 电网侧欠频 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit13 | RO | STS: Grid over frequency | STS: 电网侧过频 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit14 | RO | STS: Frequently switching Fault | STS: 频繁切换故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53100 | bit15 | RO | STS: Grid power down | STS: 电网掉电 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit0 | RO | STS: emergency stopped(EPO) | STS: 紧急停机 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit1 | RO | STS: 15V auxiliary power Fault | STS: 15V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit2 | RO | STS: 24V auxiliary power Fault | STS: 24V辅助电源故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit3 | RO | STS: CAN A comm. Fault | STS: CANA通讯故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit4 | RO | STS: CAN B comm. fault | STS: CANB通讯故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit5 | RO | STS: RS-485 comm. Fault | STS: RS-485通讯故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit6 | RO | STS: DSP initializing fault | STS: DSP初始化故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit7 | RO | STS: grid interconnection switch open circuit | STS: 并网空开开路 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit8 | RO | STS: grid interconnection switch short Fault | STS: 并网空开短路 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit9 | RO | STS: Overload timeout fault | STS: 过载超时故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit10 | RO | STS: Synchronous signal 1 fault | STS: 同步信号1故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit11 | RO | STS: Ambient temp. sensor fault | STS: 环温探头故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit12 | RO | STS: Cabinet temp. sensor fault | STS: 柜温探头故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit13 | RO | STS: Cabinet over temperature | STS: 机柜过温故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit14 | RO | STS: Module over temperature | STS: 模块温度过温 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53101 | bit15 | RO | STS: Fan Fault | STS: 风扇故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit0 | RO | STS: DSP version Fault | STS: DSP版本故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit1 | RO | STS: CPLD version Fault | STS: CPLD版本故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit2 | RO | STS: Bypass Fault | STS: 旁路故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit3 | RO | STS: SPT Fault | STS: 防雷器故障 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit4 | RO | STS: Module temp. sensor fault | STS: 模块温度探头故障 | / | 0: Normal, 1: Fault | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit5 | RO | STS: Grid voltage distortion | STS: 电网电压畸变 | / | 0: Normal, 1: Alarm | / | / | / | [5 empty] | STS | STS
143 | 53102 | bit6~15 | RO | reserved | / | / | / | / | / | /
143 | 53103 | bit0~15 | RO | reserved | / | / | / | / | / | /
143 | 53104 | bit0~15 | RO | reserved | / | / | / | / | / | /
143 | 53105 | bit0 | RO | STS: online | STS: 在线 | / | 0: False, 1: True | / | / | / | [5 empty] | STS | STS
143 | 53105 | bit1 | RO | STS: grid-tied | STS: 并网 | / | 0: False, 1: True | / | / | / | 系统综合，不开放
143 | 53105 | bit2 | RO | STS: off-grid | STS: 离网 | / | 0: False, 1: True | / | / | / | 系统综合，不开放
143 | 53105 | bit3 | RO | STS: alram | STS: 告警 | / | 0: False, 1: True | / | / | / | [5 empty] | STS | STS
143 | 53105 | bit4 | RO | STS: fault | STS: 故障 | / | 0: False, 1: True | / | / | / | [5 empty] | STS | STS
143 | 53105 | bit5 | RO | reserved | / | / | / | / | / | /
143 | 53105 | bit6 | RO | reserved | / | / | / | / | / | /
143 | 53105 | bit7 | RO | reserved | / | / | / | / | / | /
143 | 53105 | bit8 | RO | STS: grid switch status | STS: 电网开关状态 | / | 0: Open, 1: Closed | / | / | / | [5 empty] | STS | STS
143 | 53105 | bit9 | RO | STS: load switch status | STS: 负载开关状态 | / | 0: Open, 1: Closed | / | / | / | [5 empty] | STS | STS
143 | 53105 | bit10 | RO | STS: load string 1 switch status | STS: 负载支路1空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53105 | bit11 | RO | STS: load string 2 switch status | STS: 负载支路2空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53105 | bit12 | RO | STS: load string 3 switch status | STS: 负载支路3空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53105 | bit13 | RO | STS: load string 4 switch status | STS: 负载支路4空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53105 | bit14 | RO | STS: load string 5 switch status | STS: 负载支路5空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53105 | bit15 | RO | STS: load string 6 switch status | STS: 负载支路6空开状态 | / | 0: Open, 1: Closed | / | / | / | Rarely used，不开放
143 | 53106~53199 | / | RO | reserved | / | / | / | / | / | /
144 | 53200 | 2 Bytes | RO | AC line voltage L1 to L2 | AB交流线电压 | uint16 | 0~600 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
145 | 53201 | 2 Bytes | RO | AC line voltage L2 to L3 | BC交流线电压 | uint16 | 0~600 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
146 | 53202 | 2 Bytes | RO | AC line voltage L3 to L1 | CA交流线电压 | uint16 | 0~600 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
147 | 53203 | 2 Bytes | RO | AC L1 current | A相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
148 | 53204 | 2 Bytes | RO | AC L2 current | B相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
149 | 53205 | 3 Bytes | RO | AC L3 current | C相交流电流 | uint16 | -1500.0~1500.0 | -1500 | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
150 | 53206 | 2 Bytes | RO | AC frequency | 交流频率 | uint16 | 40.00~70.00 | / | 0.01 | Hz |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
150 | 53207 | 2 Bytes | RO | reserved | / | / | / | / | / | /
150 | 53208 | 2 Bytes | RO | reserved | / | / | / | / | / | /
151 | 53209 | 2 Bytes | RO | L1 AC active power | A相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
152 | 53210 | 2 Bytes | RO | L2 AC active power | B相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
153 | 53211 | 2 Bytes | RO | L3 AC active power | C相交流有功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
154 | 53212 | 2 Bytes | RO | L1 AC reactive power | A相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
155 | 53213 | 2 Bytes | RO | L2 AC reactive power | B相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
156 | 53214 | 2 Bytes | RO | L3 AC reactive power | C相交流无功功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
157 | 53215 | 2 Bytes | RO | L1 AC apparent power | A相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
158 | 53216 | 2 Bytes | RO | L2 AC apparent power | B相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
159 | 53217 | 2 Bytes | RO | L3 AC apparent power | C相交流视在功率 | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
160 | 53218 | 2 Bytes | RO | L1 AC PF | A相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01 |  |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
161 | 53219 | 2 Bytes | RO | L2 AC PF | B相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01 |  |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
162 | 53220 | 2 Bytes | RO | L3 AC PF | C相交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01 |  |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
163 | 53221 | 2 Bytes | RO | Module temperature | 模块温度 | uint16 | ‐20.0~200.0 | -20 | 0.1 | ℃ | Showing the highest heatsink of the modules | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
163 | 53222 | 2 Bytes | RO | Cabinet temperature | 机柜温度 | uint16 | ‐20.0~200.0 | -20 | 0.1 | ℃ | Disabled，不开放
164 | 53223 | 2 Bytes | RO | Ambient temperature | 环境温度 | uint16 | ‐20.0~200.0 | -20 | 0.1 | ℃ |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
165 | 53224 | 2 Bytes | RO | active power setpoint | 有功功率期望 | uint16 | ‐660.0~660.0 | -660 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
166 | 53225 | 2 Bytes | RO | reactive power setpoint | 无功功率期望 | uint16 | ‐660.0~660.0 | -660 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
167 | 53226 | 2 Bytes | RO | Off-grid voltage regulation setpoint | 离网电压调节期望 | uint16 | ‐0.10~0.10 | -0.1 | 0.01 |  |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
168 | 53227 | 2 Bytes | RO | PF setpoint | PF期望 | uint16 | ‐1.00~1.00 | -1 | 0.01 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
168 | 53228 | 2 Bytes | RO | PV BUS voltage | PV母线电压 | uint16 | 0~1000.0 | / | 0.1 | V | Only for PWG series product |  |  | PWG2 |  |  | PWG2
168 | 53229 | 2 Bytes | RO | PV BUS current | PV母线电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A | Only for PWG series product |  |  | PWG2 |  |  | PWG2
168 | 53230 | 2 Bytes | RO | PV BUS power | PV母线功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW | Only for PWG series product |  |  | PWG2 |  |  | PWG2
168 | 53231 | 2 Bytes | RO | reserved | / | / | / | / | / | /
168 | 53232 | 2 Bytes | RO | reserved | / | / | / | / | / | /
168 | 53233 | 2 Bytes | RO | Control paramseter 1 setpoint | 目标控制参数1期望 | int16 | -32768~32767 | / | 1 |  | Rarely used，不开放
168 | 53234 | 2 Bytes | RO | Control paramseter 2 setpoint | 目标控制参数2期望 | int16 | -32768~32767 | / | 1 |  | Rarely used，不开放
169 | 53235 | 2 Bytes | RO | Total AC active power | 总交流有功功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
170 | 53236 | 2 Bytes | RO | Total AC reactive power | 总交流无功功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
171 | 53237 | 2 Bytes | RO | Total AC apparent power | 总交流视在功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
172 | 53238 | 2 Bytes | RO | Total AC PF | 总交流功率因数 | uint16 | -1.00~1.00 | -1 | 0.01 |  |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
173 | 53239 | 2 Bytes | RO | Accumulative charged energy through AC port Higher 2 bytes | 累积交流充电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
174 | 53240 | 2 Bytes | RO | Accumulative charged energy through AC port Lower 2 bytes | 累积交流充电电量 低两字节 | uint16 |  | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
175 | 53241 | 2 Bytes | RO | Accumulative discharged energy through AC port higher 2 bytes | 累积交流放电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
176 | 53242 | 2 Bytes | RO | Accumulative discharged energy through AC port lower 2 bytes | 累积交流放电电量 低两字节 | uint16 |  | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
176 | 53243 | 2 Bytes | RO | Accumulative charged energy through AC port | 累积交流充电电量 | uint16 | 0~2^16 | / | 1 | kWh | Only for 104 protocol，不开放
176 | 53244 | 2 Bytes | RO | Accumulative discharged energy through AC port | 累积交流放电电量 | uint16 | 0~2^16 | / | 1 | kWh | Only for 104 protocol，不开放
176 | 53245 | 2 Bytes | RO | Accumulative generated energy through PV BUS port higher 2 bytes | 累积光伏母线发电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh | Only for PWG series product |  |  | PWG2 |  |  | PWG2
176 | 53246 | 2 Bytes | RO | Accumulative generated energy through PV BUS port lower 2 bytes | 累积光伏母线发电电量 低两字节 | uint16 |  | / | 1 | kWh | Only for PWG series product |  |  | PWG2 |  |  | PWG2
177 | 53247 | 2 Bytes | RO | Usable capacity | 可用容量 | uint16 | 0~1000.0 | 0 | 0.1 | kVA |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
178 | 53248 | 2 Bytes | RO | daily charged energy through AC port | 当天交流充电电量 | uint16 | 0~2^16 | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
179 | 53249 | 2 Bytes | RO | daily discharged energy through AC port | 当天交流放电电量 | uint16 | 0~2^16 | / | 1 | kWh |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
180 | 53250 | 2 Bytes | RO | DC String 1: DC power | 直流支路1: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
181 | 53251 | 2 Bytes | RO | DC String 1: DC voltage | 直流支路1: 直流电压 | uint16 | 0~1000.0 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
182 | 53252 | 2 Bytes | RO | DC String 1: DC current | 直流支路1: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
182 | 53253 | 2 Bytes | RO | DC String 1: Accumulative charged energy through DC port Higher 2 bytes | 直流支路1: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh | 不开放
182 | 53254 | 2 Bytes | RO | DC String 1: Accumulative charged energy through DC port Lower 2 bytes | 直流支路1: 直流累计充电电量 低两字节 | uint16 |  | / | 1 | kWh | 不开放
182 | 53255 | 2 Bytes | RO | DC String 1: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路1: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | / | 1 | kWh | 不开放
182 | 53256 | 2 Bytes | RO | DC String 1: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路1: 直流累计放电电量 低两字节 | uint16 |  | / | 1 | kWh | 不开放
183 | 53257 | 2 Bytes | RO | DC String 1: DC current setpoint | 直流支路1: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
184 | 53258 | 2 Bytes | RO | DC String 1: DC power setpoint | 直流支路1: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
184 | 53259 | 2 Bytes | RO | DC String 1: DC bus voltage | 直流支路1: 直流母线电压 | uint16 | 0~1000.0 | / | 0.1 | V |  |  | PWS2 | PWG2 | Multi-String |  | PWS2PWG2Multi-String
184 | 53260 | 2 Bytes | RO | DC String 1: Accumulative charged energy through DC port | 直流支路1: 直流累计充电电量 | uint16 | 0~2^16 | / | 1 | kWh | Only for 104 protocol，不开放
184 | 53261 | 2 Bytes | RO | DC String 1: Accumulative discharged energy through DC port | 直流支路1: 直流累计放电电量 | uint16 | 0~2^16 | / | 1 | kWh | Only for 104 protocol，不开放
184 | 53262~53269 | / | RO | / | / | / | / | / | / | / | /
184 | 53270 | 2 Bytes | RO | DC String 2: DC power | 直流支路2: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53271 | 2 Bytes | RO | DC String 2: DC voltage | 直流支路2: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53272 | 2 Bytes | RO | DC String 2: DC current | 直流支路2: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53273 | 2 Bytes | RO | DC String 2: Accumulative charged energy through DC port Higher 2 bytes | 直流支路2: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53274 | 2 Bytes | RO | DC String 2: Accumulative charged energy through DC port Lower 2 bytes | 直流支路2: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53275 | 2 Bytes | RO | DC String 2: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路2: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53276 | 2 Bytes | RO | DC String 2: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路2: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53277 | 2 Bytes | RO | DC String 2: DC current setpoint | 直流支路2: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53278 | 2 Bytes | RO | DC String 2: DC power setpoint | 直流支路2: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53279 | 2 Bytes | RO | DC String 2: DC bus voltage | 直流支路2: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53280 | 2 Bytes | RO | DC String 2: Accumulative charged energy through DC port | 直流支路2: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53281 | 2 Bytes | RO | DC String 2: Accumulative discharged energy through DC port | 直流支路2: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53282~53289 | / | RO | reserved | / | / | / | / | / | /
184 | 53290 | 2 Bytes | RO | DC String 3: DC power | 直流支路3: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53291 | 2 Bytes | RO | DC String 3: DC voltage | 直流支路3: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53292 | 2 Bytes | RO | DC String 3: DC current | 直流支路3: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53293 | 2 Bytes | RO | DC String 3: Accumulative charged energy through DC port Higher 2 bytes | 直流支路3: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53294 | 2 Bytes | RO | DC String 3: Accumulative charged energy through DC port Lower 2 bytes | 直流支路3: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53295 | 2 Bytes | RO | DC String 3: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路3: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53296 | 2 Bytes | RO | DC String 3: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路3: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53297 | 2 Bytes | RO | DC String 3: DC current setpoint | 直流支路3: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53298 | 2 Bytes | RO | DC String 3: DC power setpoint | 直流支路3: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53299 | 2 Bytes | RO | DC String 3: DC bus voltage | 直流支路3: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53300 | 2 Bytes | RO | DC String 3: Accumulative charged energy through DC port | 直流支路3: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53301 | 2 Bytes | RO | DC String 3: Accumulative discharged energy through DC port | 直流支路3: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53302~53309 | / | RO | reserved | / | / | / | / | / | /
184 | 53310 | 2 Bytes | RO | DC String 4: DC power | 直流支路4: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53311 | 2 Bytes | RO | DC String 4: DC voltage | 直流支路4: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53312 | 2 Bytes | RO | DC String 4: DC current | 直流支路4: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53313 | 2 Bytes | RO | DC String 4: Accumulative charged energy through DC port Higher 2 bytes | 直流支路4: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53314 | 2 Bytes | RO | DC String 4: Accumulative charged energy through DC port Lower 2 bytes | 直流支路4: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53315 | 2 Bytes | RO | DC String 4: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路4: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53316 | 2 Bytes | RO | DC String 4: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路4: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53317 | 2 Bytes | RO | DC String 4: DC current setpoint | 直流支路4: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53318 | 2 Bytes | RO | DC String 4: DC power setpoint | 直流支路4: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53319 | 2 Bytes | RO | DC String 4: DC bus voltage | 直流支路4: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53320 | 2 Bytes | RO | DC String 4: Accumulative charged energy through DC port | 直流支路4: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53321 | 2 Bytes | RO | DC String 4: Accumulative discharged energy through DC port | 直流支路4: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53322~53329 | / | RO | reserved | / | / | / | / | / | /
184 | 53330 | 2 Bytes | RO | DC String 5: DC power | 直流支路5: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53331 | 2 Bytes | RO | DC String 5: DC voltage | 直流支路5: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53332 | 2 Bytes | RO | DC String 5: DC current | 直流支路5: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53333 | 2 Bytes | RO | DC String 5: Accumulative charged energy through DC port Higher 2 bytes | 直流支路5: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53334 | 2 Bytes | RO | DC String 5: Accumulative charged energy through DC port Lower 2 bytes | 直流支路5: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53335 | 2 Bytes | RO | DC String 5: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路5: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53336 | 2 Bytes | RO | DC String 5: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路5: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53337 | 2 Bytes | RO | DC String 5: DC current setpoint | 直流支路5: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53338 | 2 Bytes | RO | DC String 5: DC power setpoint | 直流支路5: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53339 | 2 Bytes | RO | DC String 5: DC bus voltage | 直流支路5: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53340 | 2 Bytes | RO | DC String 5: Accumulative charged energy through DC port | 直流支路5: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53341 | 2 Bytes | RO | DC String 5: Accumulative discharged energy through DC port | 直流支路5: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53342~53349 | / | RO | reserved | / | / | / | / | / | /
184 | 53350 | 2 Bytes | RO | DC String 6: DC power | 直流支路6: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53351 | 2 Bytes | RO | DC String 6: DC voltage | 直流支路6: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53352 | 2 Bytes | RO | DC String 6: DC current | 直流支路6: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53353 | 2 Bytes | RO | DC String 6: Accumulative charged energy through DC port Higher 2 bytes | 直流支路6: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53354 | 2 Bytes | RO | DC String 6: Accumulative charged energy through DC port Lower 2 bytes | 直流支路6: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53355 | 2 Bytes | RO | DC String 6: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路6: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53356 | 2 Bytes | RO | DC String 6: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路6: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53357 | 2 Bytes | RO | DC String 6: DC current setpoint | 直流支路6: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53358 | 2 Bytes | RO | DC String 6: DC power setpoint | 直流支路6: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53359 | 2 Bytes | RO | DC String 6: DC bus voltage | 直流支路6: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53360 | 2 Bytes | RO | DC String 6: Accumulative charged energy through DC port | 直流支路6: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53361 | 2 Bytes | RO | DC String 6: Accumulative discharged energy through DC port | 直流支路6: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53362~53369 | / | / | reserved | / | / | / | / | / | /
184 | 53370 | 2 Bytes | RO | DC String 7: DC power | 直流支路7: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53371 | 2 Bytes | RO | DC String 7: DC voltage | 直流支路7: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53372 | 2 Bytes | RO | DC String 7: DC current | 直流支路7: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53373 | 2 Bytes | RO | DC String 7: Accumulative charged energy through DC port Higher 2 bytes | 直流支路7: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53374 | 2 Bytes | RO | DC String 7: Accumulative charged energy through DC port Lower 2 bytes | 直流支路7: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53375 | 2 Bytes | RO | DC String 7: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路7: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53376 | 2 Bytes | RO | DC String 7: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路7: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53377 | 2 Bytes | RO | DC String 7: DC current setpoint | 直流支路7: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53378 | 2 Bytes | RO | DC String 7: DC power setpoint | 直流支路7: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53379 | 2 Bytes | RO | DC String 7: DC bus voltage | 直流支路7: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53380 | 2 Bytes | RO | DC String 7: Accumulative charged energy through DC port | 直流支路7: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53381 | 2 Bytes | RO | DC String 7: Accumulative discharged energy through DC port | 直流支路7: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53382~53389 | / | RO | reserved | / | / | / | / | / | /
184 | 53390 | 2 Bytes | RO | DC String 8: DC power | 直流支路8: 直流功率 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53391 | 2 Bytes | RO | DC String 8: DC voltage | 直流支路8: 直流电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53392 | 2 Bytes | RO | DC String 8: DC current | 直流支路8: 直流电流 | uint16 | ‐2000.0~2000.0 | -2000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53393 | 2 Bytes | RO | DC String 8: Accumulative charged energy through DC port Higher 2 bytes | 直流支路8: 直流累计充电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53394 | 2 Bytes | RO | DC String 8: Accumulative charged energy through DC port Lower 2 bytes | 直流支路8: 直流累计充电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53395 | 2 Bytes | RO | DC String 8: Accumulative discharged energy through DC port Higher 2 bytes | 直流支路8: 直流累计放电电量 高两字节 | uint16 | 0~2^32 | 0 | 1 | kWh | 不开放
184 | 53396 | 2 Bytes | RO | DC String 8: Accumulative discharged energy through DC port Lower 2 bytes | 直流支路8: 直流累计放电电量 低两字节 | uint16 |  | 0 | 1 | kWh | 不开放
184 | 53397 | 2 Bytes | RO | DC String 8: DC current setpoint | 直流支路8: 直流电流期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
184 | 53398 | 2 Bytes | RO | DC String 8: DC power setpoint | 直流支路8: 直流功率期望 | uint16 | -1000.0~+1000.0 | -1000 | 0.1 | kW |  |  |  |  | Multi-String |  | Multi-String
184 | 53399 | 2 Bytes | RO | DC String 8: DC bus voltage | 直流支路8: 直流母线电压 | uint16 | 0~1000.0 | 0 | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
184 | 53400 | 2 Bytes | RO | DC String 8: Accumulative charged energy through DC port | 直流支路8: 直流累计充电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53401 | 2 Bytes | RO | DC String 8: Accumulative discharged energy through DC port | 直流支路8: 直流累计放电电量 | uint16 | 0~2^16 | 0 | 1 | kWh | Only for 104 protocol，不开放
184 | 53402~53409 | / | RO | reserved | / | / | / | / | / | /
184 | 53410 | 2 Bytes | RO | Gird Total active power | 电网三相总有功功率 | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kW | 无STS微网逆变器非标功能
184 | 53411 | 2 Bytes | RO | Gird L1 current | 电网A相电流 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | 无STS微网逆变器非标功能
184 | 53412 | 2 Bytes | RO | Gird L2 current | 电网B相电流 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | 无STS微网逆变器非标功能
184 | 53413 | 2 Bytes | RO | Gird L3 current | 电网C相电流 | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | 无STS微网逆变器非标功能
184 | 53414~53499 | / | RO | reserved | / | / | / | / | / | /
184 | 53500 | 2 Bytes | RO | Line voltage between L1 to L2(Grid) | AB线电压(电网侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53501 | 2 Bytes | RO | Line voltage between L2 to L3(Grid) | BC线电压(电网侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53502 | 2 Bytes | RO | Line voltage between L3 to L1(Grid) | CA线电压(电网侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53503 | 2 Bytes | RO | L1 current(Grid) | A相电流(电网侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53504 | 2 Bytes | RO | L2 current(Grid) | B相电流(电网侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53505 | 2 Bytes | RO | L3 current(Grid) | C相电流(电网侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53506 | 2 Bytes | RO | Frequency(Grid) | 频率(电网侧) | uint16 | 40.00~70.00 | 0 | 0.01 | Hz | [5 empty] | STS | STS
184 | 53507~53508 | / | RO | reserved | / | / | / | / | / | /
184 | 53509 | 2 Bytes | RO | L1 active power(Grid) | A相有功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53510 | 2 Bytes | RO | L2 active power(Grid) | B相有功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53511 | 2 Bytes | RO | L3 active power(Grid) | C相有功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53512 | 2 Bytes | RO | L1 reactive power(Grid) | A相无功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53513 | 2 Bytes | RO | L2 reactive power(Grid) | B相无功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53514 | 2 Bytes | RO | L3 reactive power(Grid) | C相无功功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53515 | 2 Bytes | RO | L1 apparent power(Grid) | A相视在功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53516 | 2 Bytes | RO | L2 apparent power(Grid) | B相视在功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53517 | 2 Bytes | RO | L3 apparent power(Grid) | C相视在功率(电网侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53518 | 2 Bytes | RO | L1 PF(Grid) | A相功率因数(电网侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53519 | 2 Bytes | RO | L2 PF(Grid) | B相功率因数(电网侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53520 | 2 Bytes | RO | L3 PF(Grid) | C相功率因数(电网侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53521 | 2 Bytes | RO | Total active power(Grid) | 总有功功率(电网侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kW | [5 empty] | STS | STS
184 | 53522 | 2 Bytes | RO | Total reactive power(Grid) | 总无功功率(电网侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53523 | 2 Bytes | RO | Total apparent power(Grid) | 总视在功功率(电网侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53524 | 2 Bytes | RO | Total PF (Grid) | 总功率因数(电网侧) | uint16 | -1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53525~53549 | / | RO | reserved | / | / | / | / | / | /
184 | 53550 | 2 Bytes | RO | Line voltage between L1 to L2(Load) | AB线电压(负载侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53551 | 2 Bytes | RO | Line voltage between L2 to L3(Load) | BC线电压(负载侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53552 | 2 Bytes | RO | Line voltage between L3 to L1(Load) | CA线电压(负载侧) | uint16 | 0~600.0 | 0 | 0.1 | V | [5 empty] | STS | STS
184 | 53553 | 2 Bytes | RO | L1 current(Load) | A相电流(负载侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53554 | 2 Bytes | RO | L2 current(Load) | B相电流(负载侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53555 | 2 Bytes | RO | L3 current(Load) | C相电流(负载侧) | uint16 | ‐1500.0~1500.0 | -1500 | 0.1 | A | [5 empty] | STS | STS
184 | 53556 | 2 Bytes | RO | Frequency(Load) | 频率(负载侧) | uint16 | 40.00~70.00 | 0 | 0.01 | Hz | [5 empty] | STS | STS
184 | 53557~53558 | / | / | reserved | / | / | / | / | / | /
184 | 53559 | 2 Bytes | RO | L1 active power(Load) | A相有功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53560 | 2 Bytes | RO | L2 active power(Load) | B相有功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53561 | 2 Bytes | RO | L3 active power(Load) | C相有功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kW | [5 empty] | STS | STS
184 | 53562 | 2 Bytes | RO | L1 reactive power(Load) | A相无功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53563 | 2 Bytes | RO | L2 reactive power(Load) | B相无功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53564 | 2 Bytes | RO | L3 reactive power(Load) | C相无功功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53565 | 2 Bytes | RO | L1 apparent power(Load) | A相视在功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53566 | 2 Bytes | RO | L2 apparent power(Load) | B相视在功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53567 | 2 Bytes | RO | L3 apparent power(Load) | C相视在功率(负载侧) | uint16 | ‐400.0~400.0 | -400 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53568 | 2 Bytes | RO | L1 PF(Load) | A相功率因数(负载侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53569 | 2 Bytes | RO | L2 PF(Load) | B相功率因数(负载侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53570 | 2 Bytes | RO | L3 PF(Load) | C相功率因数(负载侧) | uint16 | ‐1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
184 | 53571 | 2 Bytes | RO | Total active power(Load) | 总有功功率(负载侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kW | [5 empty] | STS | STS
184 | 53572 | 2 Bytes | RO | Total reactive power(Load) | 总无功功率(负载侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kvar | [5 empty] | STS | STS
184 | 53573 | 2 Bytes | RO | Total apparent power(Load) | 总视在功功率(负载侧) | uint16 | ‐1200.0~1200.0 | -1200 | 0.1 | kVA | [5 empty] | STS | STS
184 | 53574 | 2 Bytes | RO | Total PF (Load) | 总功率因数(负载侧) | uint16 | -1.00~1.00 | -1 | 0.01 | [6 empty] | STS | STS
185 | 53590 | 2 Bytes | RO | Monitor soft code | 监控软件代码 | uint16 | 0~2^16 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
186 | 53591 | 2 Bytes | RO | AC soft code | AC软件代码 | uint16 | 0~2^16 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
187 | 53592 | 2 Bytes | RO | DC soft code | DC软件代码 | uint16 | 0~2^16 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
188 | 53593 | 2 Bytes | RO | U2 soft code | U2软件代码 | uint16 | 0~2^16 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
189 | 53594 | 2 Bytes | RO | STS soft code | STS软件代码 | uint16 | 0~2^16 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2

## RW registers (hidden)
| Address | Size | Access | Register Name | 寄存器名称 | Type | Range | Offset | Accuracy | Unit | Comments Function Code: 0x06 (Actual Value = Value * Accuracy) | PWS1 flag | PWS2 flag | PWG2 flag | multi-String flag | STS flag | Assistance Column
1 | 53600 | 2 Bytes | RW | Grid interconnection mode | 并离网模式：0-并网，1-离网 | Int16 | 0: Grid-tied, 1: Off-grid | / | / | / | This register will not be saved after hard reboot | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
2 | 53601 | 2 Bytes | RW | Energy dispatching mode | 能量调度模式：0-交流调度，1-直流调度 | Int16 | 0: AC dispatching, 1: DC dispatching | / | / | / | Making AC/DC port the controlling target, Use AC dispatching if there is no special request | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
2 | 53602~53613 | / | / | / | / | / | / | / | / | / | /
2 | 53614 | 2 Bytes | RW | Control parameter 7 | 控制参数7设置 | Int16 | -32768~32767 | / | / | / | Rarely used
2 | 53615 | 2 Bytes | RW | Control parameter 6 | 控制参数6设置 | Int16 | -32768~32767 | / | / | / | Rarely used
2 | 53616 | 2 Bytes | RW | Control parameter 5 | 控制参数5设置 | Int16 | -32768~32767 | / | / | / | Rarely used
2 | 53617 | 2 Bytes | RW | Control parameter 4 | 控制参数4设置 | Int16 | -32768~32767 | / | / | / | Rarely used
2 | 53618 | 2 Bytes | RW | Control parameter 2 | 控制参数2设置 | Int16 | -32768~32767 | / | / | / | Rarely used
2 | 53619 | 2 Bytes | RW | Control parameter 1 | 控制参数1设置 | Int16 | -32768~32767 | / | / | / | Rarely used
3 | 53620 | 2 Bytes | RW | Reactive power control mode | 无功控制模式：0-恒PF控制，1-恒无功功率控制，2-电压/无功调节，3-PF曲线控制 | Int16 | 0: Constant PF control, 1: Constant reactive power control, 2: Volt/Var control， 3：PF Curve control(Australia) | / | / | / | Volt/Var control means reactive power will be regulated by grid voltage . PF Curve control only for Australia. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
4 | 53621 | 2 Bytes | RW | PF setting | 功率因数设置（正吸收感性无功，负吸收容性无功） | Int16 | -1.00~ +1.00； +: lagging, -: leading | / | 0.01 | / | Available in AC dispatching mode(53601) and constant PF control mode(53620) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
5 | 53622 | 2 Bytes | RW | Active power setting | 有功功率设置 | Int16 | ‐770.0~770.0. +: charge, power from grid to battery. -: discharge, power from battery to grid | / | 0.1 | kW | Available in AC dispatching mode(53601) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
6 | 53623 | 2 Bytes | RW | Reactive power setting | 无功功率设置（正吸收感性无功，负吸收容性无功） | Int16 | ‐770.0~770.0 +: lagging, -: leading | / | 0.1 | kvar | Available in AC dispatching mode(53601) and Constant reactive power control mode(53620) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
7 | 53624 | 2 Bytes | RW | Emergency power setting | 紧急功率设置 | Int16 | -1~770, +: discharge, power from battery to grid, 0:pcs turn off, -:disable | / | 1 | kW | Available in AC dispatching mode(53601). Maximum response priority. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
7 | 53625 | / | / | / | / | / | / | / | / | / | /
8 | 53626 | 2 Bytes | RW | Power change mode | 功率变化模式：0-阶跃，1-斜率 | Int16 | 0: step, 1: ramp(soft-start) | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
9 | 53627 | 2 Bytes | RW | Grid recovery delay | 电网恢复延时 | Int16 | 0~600 | / | 1 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
10 | 53628 | 2 Bytes | RW | Off-grid AC voltage regulation | 离网交流电压调节 | Int16 | -0.10~0.10 | / | 0.01 | / | Available only in off-gird mode(53600). ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
10 | 53629~53630 | / | / | / | / | / | / | / | / | / | /
11 | 53631 | 2 Bytes | R/W | FVRT Limit function | 电压频率穿越限流使能 | Int16 | 0: disabled, 1: enabled | / | / | / | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
12 | 53632 | 2 Bytes | RW | FVRT function | 电压频率穿越使能 | Int16 | 0: disabled, 1: enabled | / | / | / | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
13 | 53633 | 2 Bytes | RW | Islanding detection enable | 孤岛检测使能 | Int16 | 0: disabled, 1: enabled | / | / | / | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
13 | 53634 | 2 Bytes | RW | Ground fault detection | 接地故障检测使能 | Int16 | 0: disabled, 1: enabled | / | / | / | 不开放 Keep the default value if not aware of the function of this parameter
14 | 53635 | 2 Bytes | RW | Off-grid AC voltage startup mode | 离网交流电压启动方式：0-阶跃，1-斜率 | Int16 | 0: step, 1: soft-start | / | / | / | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
15 | 53636 | 2 Bytes | RW | Active power control mode | 有功控制模式：0-设置有功调节；1-电压自动调节；2-频率自动调节；3-电压频率自动调节； | Int16 | 0: Constant active power control。 1: Volt/Watt control。 2: Freq/Watt control。 3: Volt/Watt & Freq/Watt control | / | / | / | Volt/Watt control & Freq/Watt control means active power will be regulated by grid voltage/frequency following a curve/ramp rate ，Freq/Watt > Volt/Watt | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
15 | 53637 | / | / | / | / | / | / | / | / | / | /
16 | 53638 | 2 Bytes | RW | Power ramp rate | 功率变化速率 | Uint16 | USA：0.01~2.000(rated power / s) CHN：0.01~2.000(rated power / s) Australia：0.05~60.000(rated power / minuts) | / | 0.001 | / | Available in AC dispatching mode(53601) and in ramp mode(53626). If the value is 2, which means within 0.5 seconds the system can runs to full power | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
17 | 53639 | 2 Bytes | RW | Grid reconnection power ramp rate | 电网重连功率变化速率 | Int16 | USA：0.001~2.000(rated power / s) CHN：/ Australia：/ | / | 0.001 | rated power/s | Available in AC dispatching mode(53601) and in ramp mode(53626). Available when Grid reconnection. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
17 | 53640 | 2 Bytes | RW | Micro-grid control commands | 微网控制命令 | Uint16 | bit0-微网下垂命令：0-否，1-下垂； bit1-微网准同期命令：0-否，1-同期； bit2~bit15-预留; | / | 1 |  | 仅用于并离网切换控制
17 | 53641 | 2 Bytes | RW | Quasi-synch grid Voltage | 准同期电网电压参考 | Uint16 | 0~65535 | / | 1 |  | 仅用于并离网切换控制
17 | 53642 | 2 Bytes | RW | Quasi-synch AC bus Voltage | 准同期交流母线电压参考 | Uint16 | 0~65535 | / | 1 |  | 仅用于并离网切换控制
17 | 53643 | 2 Bytes | RW | Quasi-sync grid frequency | 准同期电网频率参考 | Uint16 | 0~65535 | / | 0.01 |  | 仅用于并离网切换控制
17 | 53644 | 2 Bytes | RW | Quasi-sync AC bus frequency | 准同期交流母线频率参考 | Uint16 | 0~65535 | / | 0.01 |  | 仅用于并离网切换控制
17 | 53645~53649 | / | / | / | / | / | / | / | / | / | /
18 | 53650 | 2 Bytes | RW | DC String 1: DC control mode | 直流支路1: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
19 | 53651 | 2 Bytes | RW | DC String 1: DC current setting | 直流支路1: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
20 | 53652 | 2 Bytes | RW | DC String 1: DC power setting | 直流支路1: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
21 | 53653 | 2 Bytes | RW | DC String 1: DC lower voltage threshold | 直流支路1: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
21 | 53653 | 2 Bytes | RW | DC String 1: MPPT lower voltage threshold | 直流支路1: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
21 | 53654 | 2 Bytes | RW | DC String 1: PV wake up voltage | 直流支路1: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
22 | 53655 | 2 Bytes | RW | DC String 1: end-of-discharge voltage | 直流支路1: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
22 | 53655 | 2 Bytes | RW | DC String 1: PV sleep voltage | 直流支路1: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
23 | 53656 | 2 Bytes | RW | DC String 1: precharge voltage | 直流支路1: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
24 | 53657 | 2 Bytes | RW | DC String 1: Precharge turn to fast charge judgement voltage | 直流支路1: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
25 | 53658 | 2 Bytes | RW | DC String 1: precharge time | 直流支路1: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
26 | 53659 | 2 Bytes | RW | DC String 1: float charge voltage | 直流支路1: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
26 | 53659 | 2 Bytes | RW | DC String 1: MPPT higher voltage threshold | 直流支路1: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
26 | 53659 | 2 Bytes | RW | DC String 1: DC output voltage | 直流支路1: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
27 | 53660 | 2 Bytes | RW | DC String 1: topping charge voltage | 直流支路1: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
27 | 53660 | 2 Bytes | RW | DC String 1: PV maximun voltage | 直流支路1: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
27 | 53660 | 2 Bytes | RW | DC String 1: DC maximun output voltage | 直流支路1: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
28 | 53661 | 2 Bytes | RW | DC String 1: topping charge turn to float charge judgement current | 直流支路1: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
29 | 53662 | 2 Bytes | RW | DC String 1: end-of-charge current | 直流支路1: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
30 | 53663 | 2 Bytes | RW | DC String 1: maximum charge current | 直流支路1: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
30 | 53663 | 2 Bytes | RW | DC String 1: maximum charge current | 直流支路1: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
31 | 53664 | 2 Bytes | RW | DC String 1: maximum discharge current | 直流支路1: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
31 | 53664 | 2 Bytes | RW | DC String 1: PV maximun current | 直流支路1: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
31 | 53664 | 2 Bytes | RW | DC String 1: maximum discharge current | 直流支路1: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
32 | 53665 | 2 Bytes | RW | DC String 1: maximum precharge current | 直流支路1: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
32 | 53666~53669 | / | / | / | / | / | / | / | / | / | /
33 | 53670 | 2 Bytes | RW | Over voltage region 1 protection voltage ratio | 过压保护I段电压比率 | Int16 | USA：1.05~1.25； CHN：1.05~1.35； Australia：1.05~1.20； UK：1.05~1.35； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
34 | 53671 | 2 Bytes | RW | Over voltage region 1 protection time | 过压保护I段保护时间 | Int16 | USA：0.01~13.00； CHN：0.01~13.00； Australia：0.01~2.00； UK：0.01~13.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
35 | 53672 | 2 Bytes | RW | Over voltage region 2 protection voltage ratio | 过压保护II段电压比率 | Int16 | USA：1.05~1.25； CHN：1.05~1.35； Australia：1.05~1.25； UK：1.05~1.35； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
36 | 53673 | 2 Bytes | RW | Over voltage region 2 protection time | 过压保护II段保护时间 | Int16 | USA：0.01~2.00； CHN：0.01~1.00； Australia：0.01~0.50； UK：0.01~1.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
37 | 53674 | 2 Bytes | RW | Under voltage region 1 protection voltage ratio | 欠压保护I段电压比率 | Int16 | USA：0.45~0.95； CHN：0.50~0.85； Australia：0.50~0.85； UK：0.45~0.95； | / | 0.01 | / | Keep the default value if not aware of the function of this parameter. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
38 | 53675 | 2 Bytes | RW | Under voltage region 1 protection time | 欠压保护I段保护时间 | Int16 | USA：0~21.00； CHN：0.01~5.00； Australia：0~5.00； UK：0.01~5.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
39 | 53676 | 2 Bytes | RW | Under voltage region 2 protection voltage ratio | 欠压保护II段电压比率 | Int16 | USA：0.45~0.95； CHN：0.20~0.50； Australia：/； UK：0.45~0.95； | / | 0.01 | / | invalid for Australia. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
40 | 53677 | 2 Bytes | RW | Under voltage region 2 protection time | 欠压保护II段保护时间 | Int16 | USA：0.01~11.00； CHN：0.01~1.00； Australia：/； UK：0.01~1.00； | / | 0.01 | s | invalid for Australia | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
41 | 53678 | 2 Bytes | RW | Under voltage region 3 protection voltage ratio | 欠压保护III段电压比率 | Int16 | USA：0.45~0.95； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
42 | 53679 | 2 Bytes | RW | Under voltage region 3 protection time | 欠压保护III段保护时间 | Int16 | USA：0~1.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
42 | 53680 | 2 Bytes | RW | DC String 2: DC control mode | 直流支路2: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
42 | 53681 | 2 Bytes | RW | DC String 2: DC current setting | 直流支路2: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
42 | 53682 | 2 Bytes | RW | DC String 2: DC power setting | 直流支路2: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
42 | 53683 | 2 Bytes | RW | DC String 2: DC lower voltage threshold | 直流支路2: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53683 | 2 Bytes | RW | DC String 2: MPPT lower voltage threshold | 直流支路2: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
42 | 53684 | 2 Bytes | RW | DC String 2: PV wake up voltage | 直流支路2: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
42 | 53685 | 2 Bytes | RW | DC String 2: end-of-discharge voltage | 直流支路2: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53685 | 2 Bytes | RW | DC String 2: PV sleep voltage | 直流支路2: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
42 | 53686 | 2 Bytes | RW | DC String 2: precharge voltage | 直流支路2: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53687 | 2 Bytes | RW | DC String 2: Precharge turn to fast charge judgement voltage | 直流支路2: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53688 | 2 Bytes | RW | DC String 2: precharge time | 直流支路2: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
42 | 53689 | 2 Bytes | RW | DC String 2: float charge voltage | 直流支路2: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53689 | 2 Bytes | RW | DC String 2: MPPT higher voltage threshold | 直流支路2: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
42 | 53689 | 2 Bytes | RW | DC String 2: DC output voltage | 直流支路2: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
42 | 53690 | 2 Bytes | RW | DC String 2: topping charge voltage | 直流支路2: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
42 | 53690 | 2 Bytes | RW | DC String 2: PV maximun voltage | 直流支路2: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
42 | 53690 | 2 Bytes | RW | DC String 2: DC maximun output voltage | 直流支路2: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
42 | 53691 | 2 Bytes | RW | DC String 2: topping charge turn to float charge judgement current | 直流支路2: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
42 | 53692 | 2 Bytes | RW | DC String 2: end-of-charge current | 直流支路2: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
42 | 53693 | 2 Bytes | RW | DC String 2: maximum charge current | 直流支路2: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
42 | 53693 | 2 Bytes | RW | DC String 2: maximum charge current | 直流支路2: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
42 | 53694 | 2 Bytes | RW | DC String 2: maximum discharge current | 直流支路2: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
42 | 53694 | 2 Bytes | RW | DC String 2: PV maximun current | 直流支路2: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
42 | 53694 | 2 Bytes | RW | DC String 2: maximum discharge current | 直流支路2: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
42 | 53695 | 2 Bytes | RW | DC String 2: maximum precharge current | 直流支路2: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
42 | 53696~53699 | / | / | / | / | / | / | / | / | / | /
43 | 53700 | 2 Bytes | RW | Over frequency region 1 protection frequency | 过频保护I段保护频率 | Int16 | USA：0.10~4.50； CHN：0.10~3.00； Australia：0.10~3.00； UK：0.10~3.00； | / | 0.01 | Hz | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
44 | 53701 | 2 Bytes | RW | Over frequency region 1 protection time | 过频保护I段保护时间 | Int16 | USA：0.01~300.00； CHN：0.01~300.00； Australia：0.01~5.00； UK：0.01~300.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
45 | 53702 | 2 Bytes | RW | Over frequency region 2 protection frequency | 过频保护II段保护频率 | Int16 | USA：0.10~4.50； CHN：0.10~3.00； Australia：/； | / | 0.01 | Hz | invalid for Australia | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
46 | 53703 | 2 Bytes | RW | Over frequency region 2 protection time | 过频保护II段保护时间 | Int16 | USA：0.00~10.00； CHN：0.00~10.00； Australia：/； UK：0.00~10.00； | / | 0.01 | s | invalid for Australia | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
47 | 53704 | 2 Bytes | RW | Under frequency region 1 protection frequency | 欠频保护I段保护频率 | Int16 | USA：‐4.50~ -0.10； CHN：‐4.50~ -0.10； Australia：‐5.00~ -0.10； UK：‐4.50~ -0.10； | / | 0.01 | Hz | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
48 | 53705 | 2 Bytes | RW | Under frequency region 1 protection time | 欠频保护I段保护时间 | Int16 | USA：0.00~600.00； CHN：0.00~600.00； Australia：0.01~5.00； UK：0.00~600.00； | / | 0.01 | s | Keep the default value if not aware of the function of this parameter | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
49 | 53706 | 2 Bytes | RW | Under frequency region 2 protection frequency | 欠频保护II段保护频率 | Int16 | USA：‐4.50~ -0.10； CHN：‐4.50~ -0.10； Australia：/； UK：‐4.50~ -0.10； | / | 0.01 | Hz | invalid for Australia | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
50 | 53707 | 2 Bytes | RW | Under frequency region 2 protection time | 欠频保护II段保护时间 | Int16 | USA：0.00~10.00； CHN：0.00~10.00； Australia：/； UK：0.00~10.00； | / | 0.01 | s | invalid for Australia | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
50 | 53708~53709 | / | / | / | / | / | / | / | / | / | /
50 | 53710 | 2 Bytes | RW | DC String 3: DC control mode | 直流支路3: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
50 | 53711 | 2 Bytes | RW | DC String 3: DC current setting | 直流支路3: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
50 | 53712 | 2 Bytes | RW | DC String 3: DC power setting | 直流支路3: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
50 | 53713 | 2 Bytes | RW | DC String 3: DC lower voltage threshold | 直流支路3: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53713 | 2 Bytes | RW | DC String 3: MPPT lower voltage threshold | 直流支路3: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
50 | 53714 | 2 Bytes | RW | DC String 3: PV wake up voltage | 直流支路3: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
50 | 53715 | 2 Bytes | RW | DC String 3: end-of-discharge voltage | 直流支路3: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53715 | 2 Bytes | RW | DC String 3: PV sleep voltage | 直流支路3: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
50 | 53716 | 2 Bytes | RW | DC String 3: precharge voltage | 直流支路3: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53717 | 2 Bytes | RW | DC String 3: Precharge turn to fast charge judgement voltage | 直流支路3: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53718 | 2 Bytes | RW | DC String 3: precharge time | 直流支路3: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
50 | 53719 | 2 Bytes | RW | DC String 3: float charge voltage | 直流支路3: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53719 | 2 Bytes | RW | DC String 3: MPPT higher voltage threshold | 直流支路3: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
50 | 53719 | 2 Bytes | RW | DC String 3: DC output voltage | 直流支路3: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
50 | 53720 | 2 Bytes | RW | DC String 3: topping charge voltage | 直流支路3: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
50 | 53720 | 2 Bytes | RW | DC String 3: PV maximun voltage | 直流支路3: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
50 | 53720 | 2 Bytes | RW | DC String 3: DC maximun output voltage | 直流支路3: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
50 | 53721 | 2 Bytes | RW | DC String 3: topping charge turn to float charge judgement current | 直流支路3: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
50 | 53722 | 2 Bytes | RW | DC String 3: end-of-charge current | 直流支路3: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
50 | 53723 | 2 Bytes | RW | DC String 3: maximum charge current | 直流支路3: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
50 | 53723 | 2 Bytes | RW | DC String 3: maximum charge current | 直流支路3: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
50 | 53724 | 2 Bytes | RW | DC String 3: maximum discharge current | 直流支路3: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
50 | 53724 | 2 Bytes | RW | DC String 3: PV maximun current | 直流支路3: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
50 | 53724 | 2 Bytes | RW | DC String 3: maximum discharge current | 直流支路3: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
50 | 53725 | 2 Bytes | RW | DC String 3: maximum precharge current | 直流支路3: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
50 | 53726~53729 | / | / | / | / | / | / | / | / | / | /
51 | 53730 | 2 Bytes | RW | Over voltage region 1 ride-through voltage ratio | 过压穿越I段电压比率 | Int16 | USA：1.10~1.20； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
52 | 53731 | 2 Bytes | RW | Over voltage region 1 ride-through until | 过压穿越I段时间 | Int16 | USA：0.00~13.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
53 | 53732 | 2 Bytes | RW | Over voltage region 2 ride-through voltage ratio | 过压穿越II段电压比率 | Int16 | USA：1.10~1.20； CHN：/； Australia：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
54 | 53733 | 2 Bytes | RW | Over voltage region 2 ride-through until | 过压穿越II段时间 | Int16 | USA：0.00~0.16； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
55 | 53734 | 2 Bytes | RW | Under voltage region 1 ride-through voltage ratio | 欠压穿越I段电压比率 | Int16 | USA：0.50~0.88； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
56 | 53735 | 2 Bytes | RW | Under voltage region 1 ride-through until | 欠压穿越I段时间 | Int16 | USA：20.00~50.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
57 | 53736 | 2 Bytes | RW | Under voltage region 2 ride-through voltage ratio | 欠压穿越II段电压比率 | Int16 | USA：0.50~0.88； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
58 | 53737 | 2 Bytes | RW | Under voltage region 2 ride-through until | 欠压穿越II段时间 | Int16 | USA：10.00~50.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
59 | 53738 | 2 Bytes | RW | Under voltage region 3 ride-through voltage ratio | 欠压穿越III段电压比率 | Int16 | USA：0.40~0.50； CHN：/； Australia：/； UK：/； | / | 0.01 | / | only for USA; ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
60 | 53739 | 2 Bytes | RW | Under voltage region 3 ride-through until | 欠压穿越III段时间 | Int16 | USA：0.1~21.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
60 | 53740 | 2 Bytes | RW | DC String 4: DC control mode | 直流支路4: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
60 | 53741 | 2 Bytes | RW | DC String 4: DC current setting | 直流支路4: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
60 | 53742 | 2 Bytes | RW | DC String 4: DC power setting | 直流支路4: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
60 | 53743 | 2 Bytes | RW | DC String 4: DC lower voltage threshold | 直流支路4: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53743 | 2 Bytes | RW | DC String 4: MPPT lower voltage threshold | 直流支路4: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
60 | 53744 | 2 Bytes | RW | DC String 4: PV wake up voltage | 直流支路4: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
60 | 53745 | 2 Bytes | RW | DC String 4: end-of-discharge voltage | 直流支路4: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53745 | 2 Bytes | RW | DC String 4: PV sleep voltage | 直流支路4: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
60 | 53746 | 2 Bytes | RW | DC String 4: precharge voltage | 直流支路4: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53747 | 2 Bytes | RW | DC String 4: Precharge turn to fast charge judgement voltage | 直流支路4: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53748 | 2 Bytes | RW | DC String 4: precharge time | 直流支路4: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
60 | 53749 | 2 Bytes | RW | DC String 4: float charge voltage | 直流支路4: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53749 | 2 Bytes | RW | DC String 4: MPPT higher voltage threshold | 直流支路4: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
60 | 53749 | 2 Bytes | RW | DC String 4: DC output voltage | 直流支路4: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
60 | 53750 | 2 Bytes | RW | DC String 4: topping charge voltage | 直流支路4: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
60 | 53750 | 2 Bytes | RW | DC String 4: PV maximun voltage | 直流支路4: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
60 | 53750 | 2 Bytes | RW | DC String 4: DC maximun output voltage | 直流支路4: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
60 | 53751 | 2 Bytes | RW | DC String 4: topping charge turn to float charge judgement current | 直流支路4: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
60 | 53752 | 2 Bytes | RW | DC String 4: end-of-charge current | 直流支路4: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
60 | 53753 | 2 Bytes | RW | DC String 4: maximum charge current | 直流支路4: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
60 | 53753 | 2 Bytes | RW | DC String 4: maximum charge current | 直流支路4: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
60 | 53754 | 2 Bytes | RW | DC String 4: maximum discharge current | 直流支路4: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
60 | 53754 | 2 Bytes | RW | DC String 4: PV maximun current | 直流支路4: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
60 | 53754 | 2 Bytes | RW | DC String 4: maximum discharge current | 直流支路4: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
60 | 53755 | 2 Bytes | RW | DC String 4: maximum precharge current | 直流支路4: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
60
60 | 53756~53757 | / | / | / | / | / | / | / | / | / | /
60 | 53758 | 2 Bytes | R/W | Grid recovery Upper limit frequency | 恢复并网上限频率 | Int16 | USA：0.1~1； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
60 | 53759 | 2 Bytes | R/W | Grid recovery Lower limit frequency | 恢复并网下限频率 | Int16 | USA：‐1~ ‐0.1； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes
61 | 53760 | 2 Bytes | RW | Over frequency region 1 ride-through frequency | 过频穿越I段频率 | Int16 | USA：0.1~6.00； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
62 | 53761 | 2 Bytes | RW | Over frequency region 1 ride-through until | 过频穿越I段穿越时间 | Int16 | USA：20.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
63 | 53762 | 2 Bytes | RW | Over frequency region 2 ride-through frequency | 过频穿越II段频率 | Int16 | USA：0.1~6.00； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
64 | 53763 | 2 Bytes | RW | Over frequency region 2 ride-through until | 过频穿越II段穿越时间 | Int16 | USA：0.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
65 | 53764 | 2 Bytes | RW | Under frequency region 1 ride-through frequency | 欠频穿越I段频率 | Int16 | USA：‐10~ ‐0.10； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
66 | 53765 | 2 Bytes | RW | Under frequency region 1 ride-through until | 欠频穿越I段穿越时间 | Int16 | USA：20.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
67 | 53766 | 2 Bytes | RW | Under frequency region 2 ride-through frequency | 欠频穿越II段频率 | Int16 | USA：‐10~ -0.10； CHN：/； Australia：/； UK：/； | / | 0.01 | Hz | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
68 | 53767 | 2 Bytes | RW | Under frequency region 2 ride-through until | 欠频穿越II段穿越时间 | Int16 | USA：0.0~1000.0； CHN：/； Australia：/； UK：/； | / | 0.1 | s | only for USA; follow the FVRT table given by HECO or CPUC or other local utility authority codes | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
68 | 53768~53769 | / | / | / | / | / | / | / | / | / | /
68 | 53770 | 2 Bytes | RW | DC String 5: DC control mode | 直流支路5: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
68 | 53771 | 2 Bytes | RW | DC String 5: DC current setting | 直流支路5: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
68 | 53772 | 2 Bytes | RW | DC String 5: DC power setting | 直流支路5: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
68 | 53773 | 2 Bytes | RW | DC String 5: DC lower voltage threshold | 直流支路5: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53773 | 2 Bytes | RW | DC String 5: MPPT lower voltage threshold | 直流支路5: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
68 | 53774 | 2 Bytes | RW | DC String 5: PV wake up voltage | 直流支路5: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
68 | 53775 | 2 Bytes | RW | DC String 5: end-of-discharge voltage | 直流支路5: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53775 | 2 Bytes | RW | DC String 5: PV sleep voltage | 直流支路5: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
68 | 53776 | 2 Bytes | RW | DC String 5: precharge voltage | 直流支路5: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53777 | 2 Bytes | RW | DC String 5: Precharge turn to fast charge judgement voltage | 直流支路5: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53778 | 2 Bytes | RW | DC String 5: precharge time | 直流支路5: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
68 | 53779 | 2 Bytes | RW | DC String 5: float charge voltage | 直流支路5: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53779 | 2 Bytes | RW | DC String 5: MPPT higher voltage threshold | 直流支路5: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
68 | 53779 | 2 Bytes | RW | DC String 5: DC output voltage | 直流支路5: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
68 | 53780 | 2 Bytes | RW | DC String 5: topping charge voltage | 直流支路5: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
68 | 53780 | 2 Bytes | RW | DC String 5: PV maximun voltage | 直流支路5: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
68 | 53780 | 2 Bytes | RW | DC String 5: DC maximun output voltage | 直流支路5: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
68 | 53781 | 2 Bytes | RW | DC String 5: topping charge turn to float charge judgement current | 直流支路5: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
68 | 53782 | 2 Bytes | RW | DC String 5: end-of-charge current | 直流支路5: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
68 | 53783 | 2 Bytes | RW | DC String 5: maximum charge current | 直流支路5: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
68 | 53783 | 2 Bytes | RW | DC String 5: maximum charge current | 直流支路5: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
68 | 53784 | 2 Bytes | RW | DC String 5: maximum discharge current | 直流支路5: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
68 | 53784 | 2 Bytes | RW | DC String 5: PV maximun current | 直流支路5: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
68 | 53784 | 2 Bytes | RW | DC String 5: maximum discharge current | 直流支路5: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
68 | 53785 | 2 Bytes | RW | DC String 5: maximum precharge current | 直流支路5: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
68 | 53786 | / | / | / | / | / | / | / | / | / | /
69 | 53787 | 2 Bytes | RW | Volt/Var regulation Volt point 1 | 电压无功调节点V1 | Int16 | USA：0.82~1.03； CHN：/； Australia：0.82~1.03； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
70 | 53788 | 2 Bytes | RW | Volt/Var regulation Volt point 2 | 电压无功调节点V2 | Int16 | USA：0.90~1.05； CHN：/； Australia：0.90~1.05； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
71 | 53789 | 2 Bytes | RW | Volt/Var regulation Volt point 3 | 电压无功调节点V3 | Int16 | USA：0.95~1.15； CHN：/； Australia：0.95~1.15； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
72 | 53790 | 2 Bytes | RW | Volt/Var regulation Volt point 4 | 电压无功调节点V4 | Int16 | USA：0.97~1.18； CHN：/； Australia：0.97~1.18； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
73 | 53791 | 2 Bytes | RW | Volt/Var regulation Q4 | 无功调节量Q4 | Int16 | USA：0.00~0.60； CHN：/； Australia：0.00~0.60； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
74 | 53792 | 2 Bytes | RW | Volt/Var regulation Q1 | 无功调节量Q1 | Int16 | USA：0.00~0.60； CHN：/； Australia：0.00~0.60； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power, Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
75 | 53793 | 2 Bytes | RW | Volt/Watt regulation start Volt point(High Volt) | 过压降有功起始调节点 | Int16 | USA：1.03~1.10； CHN：/； Australia：1.02~1.11； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage, Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
75 | 53794 | / | / | / | / | / | / | / | / | / | /
75 | 53795 | 2 Bytes | RW | Volt/Watt regulation recovery delay | 过压降有功恢复延时 | Int16 | USA：3~90.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA; Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode
76 | 53796 | 2 Bytes | RW | Freq/Watt regulation start Freq point(High Freq) | 过频降有功起始调节点 | Int16 | USA：0.01~1.00； CHN：/； Australia：0.01~1.00； UK：/； | / | 0.01 | Hz | invalid for CHN. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
77 | 53797 | 2 Bytes | RW | Freq/Watt regulation ramp rate | 过频降有功调节斜率 | Int16 | USA：0.02~0.07； CHN：/； Australia：/； UK：/； | / | 0.01 | Set power/Hz | only for USA; Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
77 | 53798~53799 | / | / | / | / | / | / | / | / | / | /
77 | 53800 | 2 Bytes | RW | DC String 6: DC control mode | 直流支路6: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
77 | 53801 | 2 Bytes | RW | DC String 6: DC current setting | 直流支路6: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
77 | 53802 | 2 Bytes | RW | DC String 6: DC power setting | 直流支路6: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
77 | 53803 | 2 Bytes | RW | DC String 6: DC lower voltage threshold | 直流支路6: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53803 | 2 Bytes | RW | DC String 6: MPPT lower voltage threshold | 直流支路6: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
77 | 53804 | 2 Bytes | RW | DC String 6: PV wake up voltage | 直流支路6: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
77 | 53805 | 2 Bytes | RW | DC String 6: end-of-discharge voltage | 直流支路6: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53805 | 2 Bytes | RW | DC String 6: PV sleep voltage | 直流支路6: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
77 | 53806 | 2 Bytes | RW | DC String 6: precharge voltage | 直流支路6: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53807 | 2 Bytes | RW | DC String 6: Precharge turn to fast charge judgement voltage | 直流支路6: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53808 | 2 Bytes | RW | DC String 6: precharge time | 直流支路6: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
77 | 53809 | 2 Bytes | RW | DC String 6: float charge voltage | 直流支路6: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53809 | 2 Bytes | RW | DC String 6: MPPT higher voltage threshold | 直流支路6: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
77 | 53809 | 2 Bytes | RW | DC String 6: DC output voltage | 直流支路6: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
77 | 53810 | 2 Bytes | RW | DC String 6: topping charge voltage | 直流支路6: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
77 | 53810 | 2 Bytes | RW | DC String 6: PV maximun voltage | 直流支路6: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
77 | 53810 | 2 Bytes | RW | DC String 6: DC maximun output voltage | 直流支路6: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
77 | 53811 | 2 Bytes | RW | DC String 6: topping charge turn to float charge judgement current | 直流支路6: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
77 | 538182 | 2 Bytes | RW | DC String 6: end-of-charge current | 直流支路6: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
77 | 53813 | 2 Bytes | RW | DC String 6: maximum charge current | 直流支路6: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
77 | 53813 | 2 Bytes | RW | DC String 6: maximum charge current | 直流支路6: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
77 | 53814 | 2 Bytes | RW | DC String 6: maximum discharge current | 直流支路6: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
77 | 53814 | 2 Bytes | RW | DC String 6: PV maximun current | 直流支路6: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
77 | 53814 | 2 Bytes | RW | DC String 6: maximum discharge current | 直流支路6: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
77 | 53815 | 2 Bytes | RW | DC String 6: maximum precharge current | 直流支路6: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
77 | 53816~53819 | / | / | / | / | / | / | / | / | / | /
78 | 53820 | 2 Bytes | RW | Freq/Watt regulation end Freq point(High Freq) | 过频降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：1.00~2.00； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
79 | 53821 | 2 Bytes | RW | Freq/Watt regulation start Freq point(Low Freq) | 欠频降有功起始调节点 | Int16 | USA：/； CHN：/； Australia：1.00~‐0.10； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
80 | 53822 | 2 Bytes | RW | Freq/Watt regulation end Freq point(Low Freq) | 欠频降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：‐3.00~‐1.00； UK：/； | / | 0.01 | / | only for Australia. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
81 | 53823 | 2 Bytes | RW | Over Voltage for 10 minutes | 10分钟过压幅值 | Int16 | USA：/； CHN：/； Australia：1.05~1.15； UK：/； | / | 0.01 | / | only for Australia. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
82 | 53824 | 2 Bytes | RW | PF curve regulation Power Point 1 | PF曲线模式功率调节点P1 | Int16 | USA：/； CHN：/； Australia：0.10~0.40； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
83 | 53825 | 2 Bytes | RW | PF curve regulation Power Point 2 | PF曲线模式功率调节点P2 | Int16 | USA：/； CHN：/； Australia：0.40~0.60； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
84 | 53826 | 2 Bytes | RW | PF curve regulation Power Point 3 | PF曲线模式功率调节点P3 | Int16 | USA：/； CHN：/； Australia：0.60~0.80； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
85 | 53827 | 2 Bytes | RW | PF curve regulation Power Point 4 | PF曲线模式功率调节点P4 | Int16 | USA：/； CHN：/； Australia：0.80~1.00； UK：/； | / | 0.01 | / | only for Australia. ratio * rated power. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
86 | 53828 | 2 Bytes | RW | PF curve regulation PF Point 1 | PF曲线模式功率因数PF1 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
87 | 53829 | 2 Bytes | RW | PF curve regulation PF Point 2 | PF曲线模式功率因数PF2 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
87 | 53830 | 2 Bytes | RW | DC String 7: DC control mode | 直流支路7: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
87 | 53831 | 2 Bytes | RW | DC String 7: DC current setting | 直流支路7: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
87 | 53832 | 2 Bytes | RW | DC String 7: DC power setting | 直流支路7: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
87 | 53833 | 2 Bytes | RW | DC String 7: DC lower voltage threshold | 直流支路7: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53833 | 2 Bytes | RW | DC String 7: MPPT lower voltage threshold | 直流支路7: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
87 | 53834 | 2 Bytes | RW | DC String 7: PV wake up voltage | 直流支路7: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
87 | 53835 | 2 Bytes | RW | DC String 7: end-of-discharge voltage | 直流支路7: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53835 | 2 Bytes | RW | DC String 7: PV sleep voltage | 直流支路7: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
87 | 53836 | 2 Bytes | RW | DC String 7: precharge voltage | 直流支路7: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53837 | 2 Bytes | RW | DC String 7: Precharge turn to fast charge judgement voltage | 直流支路7: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53838 | 2 Bytes | RW | DC String 7: precharge time | 直流支路7: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
87 | 53839 | 2 Bytes | RW | DC String 7: float charge voltage | 直流支路7: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53839 | 2 Bytes | RW | DC String 7: MPPT higher voltage threshold | 直流支路7: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
87 | 53839 | 2 Bytes | RW | DC String 7: DC output voltage | 直流支路7: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
87 | 53840 | 2 Bytes | RW | DC String 7: topping charge voltage | 直流支路7: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
87 | 53840 | 2 Bytes | RW | DC String 7: PV maximun voltage | 直流支路7: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
87 | 53840 | 2 Bytes | RW | DC String 7: DC maximun output voltage | 直流支路7: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
87 | 53841 | 2 Bytes | RW | DC String 7: topping charge turn to float charge judgement current | 直流支路7: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
87 | 53842 | 2 Bytes | RW | DC String 7: end-of-charge current | 直流支路7: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
87 | 53843 | 2 Bytes | RW | DC String 7: maximum charge current | 直流支路7: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
87 | 53843 | 2 Bytes | RW | DC String 7: maximum charge current | 直流支路7: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
87 | 53844 | 2 Bytes | RW | DC String 7: maximum discharge current | 直流支路7: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
87 | 53844 | 2 Bytes | RW | DC String 7: PV maximun current | 直流支路7: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
87 | 53844 | 2 Bytes | RW | DC String 7: maximum discharge current | 直流支路7: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
87 | 53845 | 2 Bytes | RW | DC String 7: maximum precharge current | 直流支路7: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
87 | 53846~53849 | / | / | / | / | / | / | / | / | / | /
88 | 53850 | 2 Bytes | RW | PF curve regulation PF Point 3 | PF曲线模式功率因数PF3 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
89 | 53851 | 2 Bytes | RW | PF curve regulation PF Point 4 | PF曲线模式功率因数PF4 | Int16 | USA：/； CHN：/； Australia：‐0.9~0.9； UK：/； | / | 0.01 | / | only for Australia. Available only when Reactive power control mode mode(53620) is set to PF Curve control mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
90 | 53852 | 2 Bytes | RW | DRMs mode enable | DRMs模式使能 | Int16 | USA：/； CHN：/； Australia：0-disable，1-enable； UK：/； | / | / | / | only for Australia. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
91 | 53853 | 2 Bytes | RW | Volt/Watt regulation end Volt Point(Low Volt) | 欠压降有功终止调节点 | Int16 | USA：/； CHN：/； Australia：0.9~1.00； UK：/； | / | 0.01 | / | only for Australia. ratio * rated voltage | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
91 | 53852~53859 | / | / | / | / | / | / | / | / | / | /
91 | 53860 | 2 Bytes | RW | DC String 8: DC control mode | 直流支路8: 直流控制模式：0-设置电流调节，1-设置功率调节 | Int16 | 0: Set current control, 1: Set power control | / | / | / | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
91 | 53861 | 2 Bytes | RW | DC String 8: DC current setting | 直流支路8: 直流电流设置 | Int16 | ‐1500.0~1500.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | A | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
91 | 53862 | 2 Bytes | RW | DC String 8: DC power setting | 直流支路8: 直流功率设置 | Int16 | ‐1000.0~1000.0。+: charge, power from grid to battery。-: discharge, power from battery to grid | / | 0.1 | kW | Available only in DC dispatching mode(53601) |  |  |  | Multi-String |  | Multi-String
91 | 53863 | 2 Bytes | RW | DC String 8: DC lower voltage threshold | 直流支路8: 直流下限电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53863 | 2 Bytes | RW | DC String 8: MPPT lower voltage threshold | 直流支路8: MPPT下限电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type；
91 | 53864 | 2 Bytes | RW | DC String 8: PV wake up voltage | 直流支路8: 光伏唤醒电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
91 | 53865 | 2 Bytes | RW | DC String 8: end-of-discharge voltage | 直流支路8: 放电终止电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53865 | 2 Bytes | RW | DC String 8: PV sleep voltage | 直流支路8: 光伏休眠电压 | Int16 | 30.0~900.0 | / | 0.1 | V | Available only in PV input type
91 | 53866 | 2 Bytes | RW | DC String 8: precharge voltage | 直流支路8: 预充电电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53867 | 2 Bytes | RW | DC String 8: Precharge turn to fast charge judgement voltage | 直流支路8: 预充转快充电压 | Int16 | 30.0~900.0 | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53868 | 2 Bytes | RW | DC String 8: precharge time | 直流支路8: 预充电时间 | Int16 | 0~30000 | / | 1 | min |  |  |  |  | Multi-String |  | Multi-String
91 | 53869 | 2 Bytes | RW | DC String 8: float charge voltage | 直流支路8: 浮充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53869 | 2 Bytes | RW | DC String 8: MPPT higher voltage threshold | 直流支路8: MPPT电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
91 | 53869 | 2 Bytes | RW | DC String 8: DC output voltage | 直流支路8: 直流输出电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
91 | 53870 | 2 Bytes | RW | DC String 8: topping charge voltage | 直流支路8: 均充电压 | Int16 | 30.0~800.0(PWS2, PWG2); 500.0~850.0(PWS1, PWS1-NA); 600.0~900.0(PWS1-H); | / | 0.1 | V |  |  |  |  | Multi-String |  | Multi-String
91 | 53870 | 2 Bytes | RW | DC String 8: PV maximun voltage | 直流支路8: 光伏最大电压 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in PV input type
91 | 53870 | 2 Bytes | RW | DC String 8: DC maximun output voltage | 直流支路8: 直流电压上限 | Int16 | 30.0~800.0 | / | 0.1 | V | Available only in DcSource type
91 | 53871 | 2 Bytes | RW | DC String 8: topping charge turn to float charge judgement current | 直流支路8: 均充转浮充电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
91 | 53872 | 2 Bytes | RW | DC String 8: end-of-charge current | 直流支路8: 充电截止电流 | Int16 | 0.0~250.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
91 | 53873 | 2 Bytes | RW | DC String 8: maximum charge current | 直流支路8: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
91 | 53873 | 2 Bytes | RW | DC String 8: maximum charge current | 直流支路8: 最大充电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
91 | 53874 | 2 Bytes | RW | DC String 8: maximum discharge current | 直流支路8: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
91 | 53874 | 2 Bytes | RW | DC String 8: PV maximun current | 直流支路8: 光伏最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in PV input type
91 | 53874 | 2 Bytes | RW | DC String 8: maximum discharge current | 直流支路8: 最大放电电流 | Int16 | 0.0~1500.0 | / | 0.1 | A | Available only in DcSource type
91 | 53875 | 2 Bytes | RW | DC String 8: maximum precharge current | 直流支路8: 预充最大电流 | Int16 | 0.0~1500.0 | / | 0.1 | A |  |  |  |  | Multi-String |  | Multi-String
92 | 53876 | 2 Bytes | RW | Volt/Var regulation Q3 | 无功调节量Q3 | Int16 | USA：0~0.6； CHN：/； Australia：0~0.6； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power. Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
93 | 53877 | 2 Bytes | RW | Volt/Var regulation Q2 | 无功调节量Q2 | Int16 | USA：0~0.6； CHN：/； Australia：0~0.6； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated power. Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
94 | 53878 | 2 Bytes | RW | Volt/Var response time | 电压无功调节反应时间 | Int16 | USA：1~90.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
95 | 53879 | 2 Bytes | RW | Volt/Var reference voltage Vref | 电压无功调节参考电压Vref | Int16 | USA：0.95~1.05； CHN：/； Australia：/； UK：/； | / | 0.01 | V | only for USA. Available only when Reactive power regulation mode is set to Volt/Var(53620). | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
96 | 53880 | 2 Bytes | RW | Volt/Watt regulation end Volt point(High Volt) | 过压降有功终止调节点 | Int16 | USA：1.04~1.1； CHN：/； Australia：1.06~1.16； UK：/； | / | 0.01 | / | invalid for CHN. ratio * rated voltage. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
97 | 53881 | 2 Bytes | RW | Volt/Watt regulation start Power point (High Volt) | 过压降有功起始功率 | Int16 | USA：0.00~1.00； CHN：/； Australia：0.00~1.00； UK：/； | / | 0.01 | / | invalid for CHN. ratio * set power. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
98 | 53882 | 2 Bytes | RW | Volt/Watt regulation end Power point (High Volt) | 过压降有功终止功率 | Int16 | USA：0.00~1.00； CHN：/； Australia：0.00~1.00； UK：/； | / | 0.01 | / | invalid for CHN. ratio * set power. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
99 | 53883 | 2 Bytes | RW | Volt/Watt response time(High Volt) | 过压降有功反应时间 | Int16 | USA：0.5~60.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
100 | 53884 | 2 Bytes | RW | Freq/Watt response time(High Freq) | 过频降有功反应时间 | Int16 | USA：0.05~3.00； CHN：/； Australia：/； UK：/； | / | 0.01 | s | only for USA. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
100 | 53885 | 2 Bytes | RW | Anti-backcurrent command 0 | 防逆流命令0 | Uint16 | Bit0:防逆流功能使能：0否，1使能； Bir1:负载不平衡补偿；0否，1使能； Bit2:本地PF控制；0否，1使能； | / | 1 | / | 仅用于无STS微网逆变器控制
100 | 53886 | 2 Bytes | RW | Local transformer capacity set | 本地变压器容量设置 | Int16 | 0~1500 | / | 1 | Kva | 仅用于无STS微网逆变器控制
100 | 53887 | 2 Bytes | RW | Grid current CT ratio | 电网电流CT变比 | Int16 | 1~20000 | / | 1 | / | 仅用于无STS微网逆变器控制
100 | 53888 | 2 Bytes | RW | Anti-backcurrent power setting | 防逆流功率设置 | Int16 | 0~100 | / | 0.1 | kW | 仅用于无STS微网逆变器控制
100 | 53889 | 2 Bytes | RW | Local power factor setting | 本地功率因数设置 | Int16 | ‐0.5~-1.0，0.5~1.0 | / | 0.01 | / | 仅用于无STS微网逆变器控制
101 | 53900 | 2 Bytes | W | System start | 系统开机 | Int16 | 1: True, else: Invalid | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
102 | 53901 | 2 Bytes | W | System stop | 系统停机 | Int16 | 1: True, else: Invalid | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
102 | 53902 | / |  | / |  | / | / | / | / | /
103 | 53903 | 2 Bytes | W | System Clear Fault (PCS) | 系统清除故障(PCS) | Int16 | 1: True, else: Invalid | / | / | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
103 | 53904 | 2 Bytes | W | DC total control command | 直流总控制命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 发给所有直流子系统
103 | 53905 | / | / | / | / | / | / | / | / | /
103 | 53906 | 2 Bytes | W | Clear Fault (STS) | 清除故障(STS) | Int16 | 1: True, else: Invalid | / | / | / | Only for STS-built-in products
103 | 53907 | / | / | / | / | / | / | / | / | /
103 | 53908 | / | / | / | / | / | / | / | / | /
103 | 53909 | 2 Bytes | W | AC String start | 交流支路开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for PWS2 series product |  |  |  | Multi-String |  | Multi-String
103 | 53910 | 2 Bytes | W | AC String stop | 交流支路关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for PWS2 series product |  |  |  | Multi-String |  | Multi-String
103 | 53911~53919 | / | / | / |  | / | / | / | / | /
103 | 53920 | 2 Bytes | W | DC String 1: start | 直流支路1: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53921 | 2 Bytes | W | DC String 1: stop | 直流支路1: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53922 | / | / | / | / | / | / | / | / | /
103 | 53923 | 2 Bytes | W | DC String 1: clear fault | 直流支路1: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53924 | 2 Bytes | W | DC String 1: BMS status commands | 直流支路1: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53925 | 2 Bytes | W | DC String 1: Detection device commands | 直流支路1: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53925~53929 | / | / | / | / | / | / | / | / | /
103 | 53930 | 2 Bytes | W | DC String 2: start | 直流支路2: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53931 | 2 Bytes | W | DC String 2: stop | 直流支路2: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53932 | / | / | / | / | / | / | / | / | /
103 | 53933 | 2 Bytes | W | DC String 2: clear fault | 直流支路2: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53934 | 2 Bytes | W | DC String 2: BMS status commands | 直流支路2: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53935 | 2 Bytes | W | DC String 2: Detection device commands | 直流支路2: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53936~53939 | / | / | / | / | / | / | / | / | /
103 | 53940 | 2 Bytes | W | DC String 3: start | 直流支路3: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53941 | 2 Bytes | W | DC String 3: stop | 直流支路3: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53942 | / | / | / | / | / | / | / | / | /
103 | 53943 | 2 Bytes | W | DC String 3: clear fault | 直流支路3: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53944 | 2 Bytes | W | DC String 3: BMS status commands | 直流支路3: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53945 | 2 Bytes | W | DC String 3: Detection device commands | 直流支路3: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53946~53949 | / | / | / | / | / | / | / | / | /
103 | 53950 | 2 Bytes | W | DC String 4: start | 直流支路4: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53951 | 2 Bytes | W | DC String 4: stop | 直流支路4: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53952 | / | / | / | / | / | / | / | / | /
103 | 53953 | 2 Bytes | W | DC String 4: clear fault | 直流支路4: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53954 | 2 Bytes | W | DC String 4: BMS status commands | 直流支路4: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53955 | 2 Bytes | W | DC String 4: Detection device commands | 直流支路4: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53956~53959 | / | / | / | / | / | / | / | / | /
103 | 53960 | 2 Bytes | W | DC String 5: start | 直流支路5: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53961 | 2 Bytes | W | DC String 5: stop | 直流支路5: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53962 | / | / | / | / | / | / | / | / | /
103 | 53963 | 2 Bytes | W | DC String 5: clear fault | 直流支路5: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53964 | 2 Bytes | W | DC String 5: BMS status commands | 直流支路5: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53965 | 2 Bytes | W | DC String 5: Detection device commands | 直流支路5: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53966~53969 | / | / | / | / | / | / | / | / | /
103 | 53970 | 2 Bytes | W | DC String 6: start | 直流支路6: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53971 | 2 Bytes | W | DC String 6: stop | 直流支路6: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53972 | / | / | / | / | / | / | / | / | /
103 | 53973 | 2 Bytes | W | DC String 6: clear fault | 直流支路6: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53974 | 2 Bytes | W | DC String 6: BMS status commands | 直流支路6: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53975 | 2 Bytes | W | DC String 6: Detection device commands | 直流支路6: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53976~53979 | / | / | / | / | / | / | / | / | /
103 | 53980 | 2 Bytes | W | DC String 7: start | 直流支路7: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53981 | 2 Bytes | W | DC String 7: stop | 直流支路7: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53982 | / | / | / | / | / | / | / | / | /
103 | 53983 | 2 Bytes | W | DC String 7: clear fault | 直流支路7: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53984 | 2 Bytes | W | DC String 7: BMS status commands | 直流支路7: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53985 | 2 Bytes | W | DC String 7: Detection device commands | 直流支路7: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53986~53989 | / | / | / | / | / | / | / | / | /
103 | 53990 | 2 Bytes | W | DC String 8: start | 直流支路8: 开机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53991 | 2 Bytes | W | DC String 8: stop | 直流支路8: 关机 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53992 | / | / | / | / | / | / | / | / | /
103 | 53993 | 2 Bytes | W | DC String 8: clear fault | 直流支路8: 清除故障 | Int16 | 1: True, else: Invalid | / | / | / | Only for Multi-String series product |  |  |  | Multi-String |  | Multi-String
103 | 53994 | 2 Bytes | W | DC String 8: BMS status commands | 直流支路8: BMS状态命令 | Int16 | Bit0: BMS trip; 1: True, 0: Invalid; Bit1: Battery full; 1: True, 0: Invalid; Bit2: Batt empty; 1: True, 0: Invalid; Bit3~15: reserved; | / | / | / | 仅用于内部EMS控制
103 | 53995 | 2 Bytes | W | DC String 8: Detection device commands | 直流支路8: 检测装置命令 | Int16 | Bit0: Insulation test. 1: True, 0: Invalid; Bit1~15: reserved; | / | / | / | 仅用于支持选配件机型
103 | 53996~53999 | / | / | / | / | / | / | / | / | /
104 | 56000 | 2 Bytes | W | Time Setting：year | 时间设置：年 | Uint16 | 2000~2099 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
105 | 56001 | 2 Bytes | W | Time Setting：month | 时间设置：月 | Uint16 | 1~12 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
106 | 56002 | 2 Bytes | W | Time Setting：day | 时间设置：日 | Uint16 | 1~31 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
107 | 56003 | 2 Bytes | W | Time Setting：hour | 时间设置：小时 | Uint16 | 0~23 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
108 | 56004 | 2 Bytes | W | Time Setting：minute | 时间设置：分钟 | Uint16 | 0~59 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
109 | 56005 | 2 Bytes | W | Time Setting：second | 时间设置：秒 | Uint16 | 0~59 | / | 1 | / |  | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
110 | 56006 | 2 Bytes | W | BMS communication timeout setting | BMS通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the BMS communication Interruption exceeds the setting value, PCS will turn off. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
111 | 56007 | 2 Bytes | W | Remote RS485 communication timeout setting | 远程485通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the RS485 communication Interruption exceeds the setting value, and PCS works in remote mode, PCS will turn off. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
112 | 56008 | 2 Bytes | W | Remote TCP communication timeout setting | 远程TCP通信超时设置 | Uint16 | 0~600 | / | 1 | second | if the setting value is zero，the function is invalid. Otherwise, if the TCP comm. Interruption exceeds the setting value, and PCS works in remote mode, PCS will turn off. | PWS1 | PWS2 | PWG2 |  |  | PWS1PWS2PWG2
E.g Set Grid interconnection mode(53600) to off-grid：
Master Send：
| Device address | Function Code |  | Register Starting Address H | Register Starting Address L |  | Data H | Data L |  | Verification
(L->H)
| 0x01 | 0x06 |  | 0xD1 | 0x60 |  | 0x00 | 0x01 |  | CRC
Slave Reply：
| Device address | Function Code |  | Register Starting Address H | Register Starting Address L |  | Data H | Data L |  | Verification
(L->H)
| 0x01 | 0x06 |  | 0xD1 | 0x60 |  | 0x00 | 0x01 |  | CRC
Any abnormal，refer to Frame formats