## Frame format
Frame formats
The Sinexcel Energy Storage Inverters support RS485(MODBUS RTU) or Ethernet(MODBUS TCP/IP)，When implementing RS485, the bode rate is 19200bps or 9600bps, verification: MODBUS RTU CRC16，When deploying ethernet, the communication format conforms to MODBUS TCP.
本协议适用于盛弘电气股份有限公司储能变流器与上位机之间的通信。采用 RS485(MODBUS RTU) 或 Ethernet(MODBUS TCP/IP)通信规约。 如果选用RS485。波特率为19200bps或9600bps，默认19200bps。起始位：1，数据位：8，校验位：NONE，停止位：1。MODBUS数据以字为单位读写，高字节先发送，低字节后发送。校验方式采用 MODBUS RTU CRC16，低字节先发送，高字节后发送。设备地址范围1-247。 如果选用Ethernet。底层协议为TCP/IP。物理接口为LAN，10/100M自适应以太网口。在局域网内支持星型拓扑连接，储能变流器为服务器端。监听端口为502。
Refer to the attached document for more information about MODBUS TCP/IP
Table 1 Function code list
Function Code | Function
01 | Read coil status(output relay)
02 | Read input status(input relay)
03 | read holding registers(output register)
04 | read input registers
05 | Force single coil
06 | Preset single register
07 | read exception status
08 | Diagnostics
15 | Force multiple coils
16 | Preset multiple registers
101 | For self-defining
Table 2 Exception code list
Exception Code | MODBUS name | Comments
01 | Illegal Function Code | The function code is unknown by the server
02 | Illegal Data Address | Dependant on the request
03 | Illegal Data Value | Dependant on the request
04 | Server Failure | The server failed during the execution
05 | Acknowledge | The server accepted the service invocation but the service requires a relatively long time to execute. The server therefore returns only an acknowledgement of the service invocation receipt.
06 | Server Busy | The server was unable to accept the MB Request PDU. The client application has the responsibility of deciding if and when to re-send the request.
F0 | Controlling method Error | Remote control not supported
MODBUS RTU
Table 3 （for Modbus RTU）： Device Address
Fields | Length | Range
Device Address | 1 Byte | 1~0xF7
Table 4.1 （for Modbus RTU）： 0x03 Reading data request
Device address | Function Code（0x03） | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 2 Bytes
Table 4.2（for Modbus RTU）： 0x03 Reading successful response
Device address | Function Code（0x03） | data quantily | data 1 | …… | data N | Verification
|  | (register quantity*2) |  |  |  | (L->H)
1 Byte | 1 Byte | 1 Byte | 1 Byte | n Bytes | 1 Byte | 2 Bytes
Table 4.3 （for Modbus RTU）： 0x03 Reading failed response
Device address | Error Code |  | Exeption code |  |  | Verification
| Function Code+0x80（0x83） |  | 01 or 02 or 03 or 04, refer to Table 2 |  |  | (L->H)
1 Byte | 1 Byte |  | 1 Byte |  |  | 2 Bytes
Table 5.1（for Modbus RTU）： 0x06 Writing Data request(Writing single value)
Device address | Function Code（0x06） | Register Starting Address H | Register Starting Address L | set data H | set data L | Verification
(L->H)
1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 2 Bytes
Table 5.2（for Modbus RTU）： 0x06 Writing successful response(Writing single value)
Device address | Function Code（0x06） | Register Starting Address H | Register Starting Address L | set data H | set data L | Verification
(L->H)
1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 1 Byte | 2 Bytes
Table 5.3 （for Modbus RTU）： 0x06 Writing failed response(Writing single value)
Device address | Error Code |  | Exeption code |  |  | Verification
| Function Code+0x80（0x86） |  | 01 or 02 or 03 or 04, refer to Table 2 |  |  | (L->H)
1 Byte | 1 Byte |  | 1 Byte |  |  | 2 Bytes
MODBUS TCP/IP
Table 3 （for Modbus TCP/IP）： MBAP header
Fields | Length | Description |  | Client | Server
Transaction Identifier | 2 Bytes | Indentification of a MODBUS request/response transaction |  | Initialized by the client | Recopied by the server from the received request
Protocol Identifier | 2 Bytes | 0= MODBUS protocol |  | Initialized by the client | Recopied by the server from the received request
Length | 2 Bytes | Number of following Bytes |  | Initialized by the client(request) | Initialized by the server(response)
Unit Identifier | 1 Byte | Identification of a remote slave connected on a serial line or on other buses |  | Initialized by the client | Recopied by the server from the received request
Table 4.1 （for Modbus TCP/IP）： Reading data request
MBAP | Function code（0x03） | Starting Address of register | Quantity of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 4.2 （for Modbus TCP/IP）： Reading successful response
MBAP | Function code（0x03） | Quantity of Data Bytes | Value of registers
7 Bytes | 1 Byte | 1 Byte | （2*N）Bytes
Table 4.3（for Modbus TCP/IP）： Reading failed response
MBAP | Error Code（0x83/0x84） |  | Exeption code（01 or 02 or 03 or 04, refer to Table 2）
7 Bytes | 1 Byte |  | 1 Byte
Table 5.1 （for Modbus TCP/IP）： Writing Data request(Writing single value)
MBAP | Function Code（0x06） | Starting Address of register | Value of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 5.2（for Modbus TCP/IP）： Writing successful response(Writing single value)
MBAP | Function Code | Starting Address of register | Value of registers
7 Bytes | 1 Byte | 2 Bytes | 2 Bytes
Table 5.3 （for Modbus TCP/IP）： Writing failed response(Writing single value)
MBAP | Error Code（0x86） |  | Exeption code（01 or 02 or 03 or 04, refer to Table 2）
7 Bytes | 1 Byte |  | 1 Byte
Table 7 Applied Function code list by Sinexcel
Function | Function Code | register range | Remark
Read-only registers | 0x03 | 0 ~ 135(RO) | Status and alarm parameters of equipment
|  | 136 ~ 1000(RO) | Analog quantity of equipment
Read-write registers | 0x06(W) 0x03 (R) | 1001 ~ 2999(R/W) | Setting-up parameters of equipment
MESA registers | 0x06(W) 0x03 (R) | ？ ~ ？(R/W) | Status and alarm parameters of equipment Setting-up parameters of equipment
BMS registers | 0x06(W) 0x03 (R) | ？ ~ ？(R/W) | Status and alarm parameters of equipment Setting-up parameters of equipment
Module registers | 0x06(W) 0x03 (R) | 3000 ~ 33999(R/W) | Status and alarm parameters of equipment Setting-up parameters of equipment
E.g: Set Grid interconnection mode(1006) to off-grid：
Master Send：
Device address | Function Code |  | Register Starting Address H | Register Starting Address L |  | Data H | Data L | Verification
(L->H)
0x01 | 0x06 |  | 0x03 | 0xEE |  | 0x00 | 0x01 | CRC
Slave Reply：
Device address | Function Code |  | Register Starting Address H | Register Starting Address L |  | Data H | Data L | Verification
(L->H)
0x01 | 0x06 |  | 0x03 | 0xEE |  | 0x00 | 0x01 | CRC

## Version Control
版本 | 更改原因 | 更改说明 | 更改人 | 更改时间
V106 | 1、优化和修改 | 1、拆分Sunspec和modbus协议 2、修改41号寄存器，分配到sunspec协议页面（V106_B） 3、删除预留部分寄存器（V106_B） 4、删除33-bit8、44-bit2、751寄存器（V106_B） 5、新增认证参数默认值页面（V106_C） 6、新增658寄存器、修改802寄存器参数范围（V106_D） 7、修改802寄存器参数范围（V106_E） 8、修改772、786、890、891、892、893寄存器的1741认证参数（V106_F） 9、修改屏幕显示故障码97命名错误，从并网参数冲突-》离网参数冲突，655待机 0-》退出待机模式（V106_G） | XXY | 2021/3/19 2021/3/29 2021/3/31 2021/4.07 2021/4/16 2021/5/08 2021/5/19
V107 | 1、新增功能 | 1、新增协能BMS支持(V107_A) 2、新增Event Bitfield2 解析定义(V107_B) 3、更正沃太的SOC、SOH的Unit定义(V107_C) 4、新增227寄存器_风扇转速（V107_D） 5、新增806交流继电器检测模式（V107_E） 6、新增800 CHN认证功能（V107_F） | XXY | 2021/6/9 2021/6/23 2021/6/30 2021/7/5 2021/7/8 2021/9/22
V108 | 1、协议修改 | 1、删除133、134寄存器_正负母线电压（V108_A） 2、修改137寄存器描述方式：-0.20~0.20->-20%~20%（V108_A） 3、删除225、226冗余寄存器（V108_A） 4、修改326寄存器，0-modbus协议禁用（V108_A） 5、修改754寄存器，1-830V禁用（V108_A） 6、963寄存器类型为RO（V108_A） 7、屏蔽748~767校准参数寄存器（V108_A） 8、备注协议里面不会写EEPROM的寄存器135、136、137、138、878、811、812（V108_B） 9、修改协议寄存器范围描述错误：871:-0.26~4.00-》-0.26~-4.00；892：0.00~0.30 -> 0.00~3.00（V108_C） 10、修改853~856,883~886寄存器描述错误：+(lagging),-(leading)-> +(leading),-(lagging)（V108_C） | XXY | 2021/10/27 2021/11/15 2021/12/07

## PCS30kW-COMM_PROTOCOL
Address | Size | Access | Type | Register Name | 寄存器名称 | Precision | 精度 | Comments Function Code: 0x03(R)\0x06(W)
1 | 16world | RO | String | Manufacturer and model number | 版本型号 | / | /
17 | 8world | RO | String | Serial Number | 序列号 | / | /
32 | Bit0 | RO | Bitfield | Fault status | 故障综合 | 1- Fault，0- Normal | 1- 故障，0- 正常
32 | Bit1 | RO | Bitfield | Alert status | 告警综合 | 1- Alarm，0- Normal | 1- 告警，0- 正常
32 | Bit2 | RO | Bitfield | ON/OFF status | 启停状态 | 1- ture，0- false | 1- 是，0- 否
32 | Bit3 | RO | Bitfield | Grid-tied status | 并网状态 | 1- ture，0- false | 1- 是，0- 否
32 | Bit4 | RO | Bitfield | Off-grid(Island mode) | 离网状态 | 1- ture，0- false | 1- 是，0- 否
32 | Bit5 | RO | Bitfield | Derating status | 降额状态 | 1- ture，0- false | 1- 是，0- 否
32 | Bit6 | RO | Bitfield | Allow grid connection judgment | 允许并网判断 | 1- ture，0- false | 1- 是，0- 否
32 | Bit7 | RO | Bitfield | Standby status | 待机状态 | 1- ture，0- false | 1- 是，0- 否
33 | Bit0 | RO | Bitfield | Obtain fault record flag | 获取故障记录标志 | 1- ture，0- false | 1- 是，0- 否
33 | Bit1 | RO | Bitfield | Write power generation into EEPROM | 写发电量进EEPROM | 1- ture，0- false | 1- 是，0- 否
33 | Bit2 | RO | Bitfield | Initialize DSP parameters | 初始化DSP参数 | 1- ture，0- false | 1- 是，0- 否
33 | Bit3 | RO | Bitfield | Master-slave mode | 主从模式 | 1-Master,0- Slave, | 1- 主机，0- 从机
36 | bit0 | RO | Bitfield | AC OVP | 交流侧过压保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit1 | RO | Bitfield | AC UVP | 交流侧欠压保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit2 | RO | Bitfield | AC OFP | 交流侧过频保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit3 | RO | Bitfield | AC UFP | 交流侧欠频保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit4 | RO | Bitfield | Grid voltage unbalance | 电网电压不平衡 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit5 | RO | Bitfield | Grid phase reverse | 电网电压反序 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit6 | RO | Bitfield | Inverter island | 逆变器孤岛 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit7 | RO | Bitfield | On/off grid switchover failure | 并离网切换故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit8 | RO | Bitfield | Output ground fault | 输出接地故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit9 | RO | Bitfield | Grid phase lock failed | 电网锁相失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit10 | RO | Bitfield | Internal air over-temp | 内部环境温度过温 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit11 | RO | Bitfield | Grid-connected condition judgment timeOut | 并网条件判断超时 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit12 | RO | Bitfield | Module renumber failure | 模块重号故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit13 | RO | Bitfield | CANB communication failure | CANB通信故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit14 | RO | Bitfield | Power frequency synchronization failure | 工频同步故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
36 | Bit15 | RO | Bitfield | Carrier synchronization failure | 载波同步故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit0 | RO | Bitfield | EPO | 紧急停机 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit1 | RO | Bitfield | Monitor Parameter mismatch | 监控参数设置不匹配 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit2 | RO | Bitfield | DSP version abnormal | DSP版本异常 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit3 | RO | Bitfield | CPLD version error | CPLD版本异常 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit4 | RO | Bitfield | Hardware Version error | 硬件版本错误 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit5 | RO | Bitfield | CAN A comm. Fault | CANA通信故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit6 | RO | Bitfield | Auxiliary power fault | 辅助电源故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit7 | RO | Bitfield | Fan failure | 风扇故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit8 | RO | Bitfield | BUS over voltage | 母线过压 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit9 | RO | Bitfield | BUS low voltage | 母线欠压 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit10 | RO | Bitfield | BUS voltage unbanlaced | 母线电压不平衡 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit12 | RO | Bitfield | AC Relay short circuit | 交流继电器短路 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit13 | RO | Bitfield | Output voltage abnormal. | 输出电压异常 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit14 | RO | Bitfield | Output current unbalanced | 输出电流不平衡 | 1- Fault，0- Normal | 1- 故障，0- 正常
37 | Bit15 | RO | Bitfield | Over-temperature of heat sink | 散热器过温 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit0 | RO | Bitfield | Output Overload TOT | 输出过载超时 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit1 | RO | Bitfield | Grid continue over voltage | 电网连续过压 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit2 | RO | Bitfield | AC soft start failure | 交流软启动失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit3 | RO | Bitfield | Inverter start failure. | 逆变器启动失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit4 | RO | Bitfield | AC relay is open. | AC继电器开路 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit5 | RO | Bitfield | U2 board communication is abnormal | U2板通信异常 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit6 | RO | Bitfield | AC DC component excess | AC直流分量超额 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit7 | RO | Bitfield | Master-slave sampling abnormality | 主从采样异常 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit8 | RO | Bitfield | Parameter setting error | 参数下设错误 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit9 | RO | Bitfield | Low off-grid energy | 离网能量低 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit10 | RO | Bitfield | N line is not connected | N线未连接 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit11 | RO | Bitfield | Standby bus height | 待机母线高 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit12 | RO | Bitfield | Single-phase wiring error | 单相接线错误 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit13 | RO | Bitfield | Excessive grid frequency change rate | 电网频率变化率超额 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit14 | RO | Bitfield | Abrupt phase angle fault of power grid | 电网相角突变故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
38 | Bit15 | RO | Bitfield | Grid connection parameter conflict | 并网参数冲突 | 1- Fault，0- Normal | 1- 故障，0- 正常
39 | Bit0 | RO | Bitfield | EE Reading error 1 | EE读取错误1 | 1- Alarm，0- Normal | 1- 告警，0- 正常
39 | Bit1 | RO | Bitfield | EE Reading error 2 | EE读取错误2 | 1- Alarm，0- Normal | 1- 告警，0- 正常
39 | Bit2 | RO | Bitfield | Flash Reading error | Flash读取错误 | 1- Alarm，0- Normal | 1- 告警，0- 正常
39 | Bit3 | RO | Bitfield | Inverter over load | 逆变器过载 | 1- Alarm，0- Normal | 1- 告警，0- 正常
39 | Bit4 | RO | Bitfield | Battery parameter setting error | 电池参数设置错误 | 1- Alarm，0- Normal | 1- 告警，0- 正常
39 | Bit5 | RO | Bitfield | Slave lost alarm | 从机丢失告警 | 1- Alarm，0- Normal | 1- 告警，0- 正常
40 | Bit0 | RO | Bitfield | DC charging | DC充电中 | 1- ture，0- false | 1- 是，0- 否
40 | Bit1 | RO | Bitfield | DC discharging | DC放电中 | 1- ture，0- false | 1- 是，0- 否
40 | Bit2 | RO | Bitfield | Battery fully charged | 电池充满 | 1- ture，0- false | 1- 是，0- 否
40 | Bit3 | RO | Bitfield | Battery empty | 电池放空 | 1- ture，0- false | 1- 是，0- 否
40 | Bit4 | RO | Bitfield | DC Fault status | DC故障状态 | 1- Fault，0- Normal | 1- 故障，0- 正常
40 | Bit5 | RO | Bitfield | DC Alert status | DC告警状态 | 1- Alarm，0- Normal | 1- 告警，0- 正常
44 | Bit0 | RO | Bitfield | DC input OVP(over voltage protection) | DC输入过压保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
44 | Bit1 | RO | Bitfield | DC input UVP(under voltage protection) | DC输入欠压保护 | 1- Fault，0- Normal | 1- 故障，0- 正常
44 | Bit3 | RO | Bitfield | BMS Alerts.(available only BMS connected) | BMS告警 | 1- Fault，0- Normal | 1- 故障，0- 正常
44 | Bit4 | RO | Bitfield | BMS connection timeout | BMS连接超时 | 1- Fault，0- Normal | 1- 故障，0- 正常
44 | Bit5 | RO | Bitfield | EMS connection timeout | EMS连接超时 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit0 | RO | Bitfield | DC soft-start failed. | DC软起动失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit1 | RO | Bitfield | DC relay short-circuit. | DC继电器短路 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit2 | RO | Bitfield | DC relay short-open | DC继电器开路 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit3 | RO | Bitfield | Battery power over load. | 电池功率过载 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit4 | RO | Bitfield | DC BUS starting failed | 母线启动失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
45 | Bit5 | RO | Bitfield | DC quick check overcurrent | 直流快检过流 | 1- Fault，0- Normal | 1- 故障，0- 正常
47 | Bit0 | RO | Bitfield | DC OC | 直流过流 | 1- Alarm，0- Normal | 1- 告警，0- 正常
101 | 1 | RO | int16 | InvOutVolt_A _Rms_Value | 模块端口AB线电压 | 0.1V | 0.1V | AC A-B RMS voltage
102 | 1 | RO | int16 | InvOutVolt_B _Rms_Value | 模块端口BC线电压 | 0.1V | 0.1V | AC B-C RMS voltage
103 | 1 | RO | int16 | InvOutVolt_C_Rms_value | 模块端口CA线电压 | 0.1V | 0.1V | AC C-A RMS voltage
104 | 1 | RO | int16 | Analog_A_GridCurrent_Rms_Value | A相输出电流 | 0.1A | 0.1A | AC phA RMS current
105 | 1 | RO | int16 | Analog_B_GridCurrent_Rms_Value | B相输出电流 | 0.1A | 0.1A | AC phB RMS current
106 | 1 | RO | int16 | Analog_C_GridCurrent_Rms_Value | C相输出电流 | 0.1A | 0.1A | AC phC RMS current
107 | 1 | RO | int16 | Analog_Grid_Freq | 电网频率 | 0.01HZ | 0.01HZ | AC frequency
110 | 1 | RO | int16 | Analog_A_ActivePower_Rms_Value | A相有功功率 | 0.01kW | 0.01kW | AC phA Active Power
111 | 1 | RO | int16 | Analog_B_ActivePower_Rms_Value | B相有功功率 | 0.01kW | 0.01kW | AC phB Active Power
112 | 1 | RO | int16 | Analog_C_ActivePower_Rms_Value | C相有功功率 | 0.01kW | 0.01kW | AC phC Active Power
113 | 1 | RO | int16 | Analog_A_ReactivePower_Rms_Value | A相无功功率 | 0.01kVAR | 0.01kVAR | AC phA Reactive Power
114 | 1 | RO | int16 | Analog_B_ReactivePower_Rms_Value | B相无功功率 | 0.01kVAR | 0.01kVAR | AC phB Reactive Power
115 | 1 | RO | int16 | Analog_C_ReactivePower_Rms_Value | C相无功功率 | 0.01kVAR | 0.01kVAR | AC phC Reactive Power
116 | 1 | RO | int16 | Analog_A_ApparentPower | A相视在功率 | 0.01kVA | 0.01kVA | AC phA Apparent Power
117 | 1 | RO | int16 | Analog_B_ApparentPower | B相视在功率 | 0.01kVA | 0.01kVA | AC phB Apparent Power
118 | 1 | RO | int16 | Analog_C_ApparentPower | C相视在功率 | 0.01kVA | 0.01kVA | AC phC Apparent Power
119 | 1 | RO | int16 | Analog_A_PF_Rms_Value | A相功率因数 | 0.01PF | 0.01PF | AC phA Power Factor
120 | 1 | RO | int16 | Analog_B_PF_Rms_Value | B相功率因数 | 0.01PF | 0.01PF | AC phB Power Factor
121 | 1 | RO | int16 | Analog_C_PF_Rms_Value | C相功率因数 | 0.01PF | 0.01PF | AC phC Power Factor
122 | 1 | RO | int16 | Analog_ ActivePower_3Phase | 三相总有功功率 | 0.01kW | 0.01kW | AC Real Power
123 | 1 | RO | int16 | Analog_ ReactivePower_3Phase | 三相总无功功率 | 0.01kVAR | 0.01kVAR | AC Reactive Power
124 | 1 | RO | int16 | Analog_ ApparentPower_3Phase | 三相总视在功率 | 0.01kVA | 0.01kVA | AC Apparent Power
125 | 1 | RO | int16 | Analog_ PowerFactor_3Phase | 三相总PF值 | 0.01PF | 0.01PF | AC Power Factor
126 | 2 | RW | uint32 | Analog_Dischg_Energy | 馈网电量 | 0.1kWh | 0.1kWh | Not quite accurate, for reference only. Write 0 to reset the value
128 | 2 | RW | uint32 | Analog_Chg_Energy | 电网供电电量 | 0.1kWh | 0.1kWh | Not quite accurate, for reference only. Write 0 to reset the value
130 | 2 | RO | uint32 | Analog_Reactive_Energy | 无功电量 | 0.1kWh | 0.1kWh | Reactive energy
132 | 1 | RO | int16 | Temperature_Of_AC_ Heat_Sink | DCAC散热器温度 | -40~125;Precision:1C | -40~125;精度:1C | 100℃ will trigger an alarm and shutdown
135 | 1 | RW | int16 | Target_Active_Power | 有功功率期望 | -30.0 ~30.0; Precision:0.1kW; default:0 | -30.0 ~30.0；精度：0.1kW；默认：0 | minus: charge, positive: discharge e.g.:10kw,write+100 to the inverter (Do not write EEPROM)
136 | 1 | RW | int16 | Target_Reactive_Power | 无功功率期望 | -30.0 ~30.0;Precision:0.1kVAr;default:0 | -30.0 ~30.0；精度：0.1kVAr；默认：0 | minus: inductive,positive: capacitive (Do not write EEPROM)
137 | 1 | RW | int16 | Target_Off-grid_Voltage | 离网电压期望 | -20% ~20%;Precision:0.01V;default:0 | -20%~20%；精度：0.01V；默认：0 | Target off-grid voltage bias (Do not write EEPROM)
138 | 1 | RW | int16 | Target_Off-grid_Frequency | 离网频率期望 | -5.00 ~5.00;Precision:0.01Hz;default:0 | -5.00 ~5.00；精度：0.01Hz；默认：0 | Target off-grid frequency bias (Do not write EEPROM)
141 | 1 | RO | int16 | Analog_DC_Power | 直流功率 | 0.01kW | 0.01kW | DC power
142 | 1 | RO | int16 | Analog_DC_Voltage | 直流电压 | 0.1V | 0.1V | DC voltage
143 | 1 | RO | int16 | Analog_DC_Current | 直流电流 | 0.1A | 0.1A | DC current
144 | 2 | RW | uint32 | Analog_DC_Chg_Energy | 直流充电电量 | 0.1kWh | 0.1kWh | The accuracy is not enough, it is for reference only, if you need an accurate value, please add an external meter
146 | 2 | RW | uint32 | Analog_ DC_Dischg_Energy | 直流放电电量 | 0.1kWh | 0.1kWh | The accuracy is not enough, it is for reference only, if you need an accurate value, please add an external meter
148 | 1 | RO | int16 | Temperature_Of_DCDC_Heat_Sink | DCDC散热器温度 | -40~125;Precision:1C | -40~125；精度:1C | 100℃ will trigger an alarm and shutdown
224 | 1 | RO | uint16 | DC relay rear-end voltage | 直流继电器后端电压 | 0.1V | 0.1V | DC relay rear-end voltage_1
227 | 1 | RO | uint16 | Fan speed | 风扇转速 | 0~1000;Precision:1 | 0~1000；精度：1 | 0-stop turning, 600-low speed, 700-medium speed, 870-high speed, 999-full speed
300 | 4 | RW | uint64 | IP_Address | IP地址 | 192.168.1.10 (Wall-mounted) | 192.168.1.11（Rack-mounted） | Takes effect after hard reset,set on the HMI（wall-mounted）,Default IP 192.168.1.10,node ID 1
304 | 4 | RW | uint64 | Netmask | 网络掩码 | 255.255.254.0(default) | 255.255.254.0(default) | Takes effect after hard reset
308 | 4 | RW | uint64 | Gateway | 网关IP地址 | 192.168.1.1(default) | 192.168.1.1(default) | Takes effect after hard reset
312 | 3 | RW | uint48 | MAC | MAC地址 | fixed first 2 bytes as 00-24, the following 4 bytes is changeable, | 前两个字节固定00-24，后4个字节可改变 | Takes effect after hard reset
316 | 1 | RW | uint16 | Modbus_Device_Address | Modbus设备地址 | 1~247, default: 1 | 1~247, 默认：1 | Takes effect after hard reset
320 | 1 | RW | enum16 | baud_Rate | 接口波特率，精度为位/秒 | 0-19200, 1-9600， Default:0 | 0-19200， 1-9600， 默认：0 | Takes effect after hard reset
325 | 1 | RW | enum16 | Interface Type | 接口类型 | 0-RS-485, 1-Ethernet， Default:1 | 0:-RS-485， 1-Ethernet， 默认：1 | Takes effect after hard reset
326 | 1 | RW | enum16 | Protocol_Selection | 串行协议选择 | 0-disable 1- sunspec， Default:1 | 0-禁用 ， 1-sunspec， 默认：1 | Takes effect after hard reset(If you write 0 by mistake, write 1 to 2388 to recover)
327 | 1 | RW | uint16 | EMS timeout setting | EMS超时时间 | 0~32767，Precision:1 ，default:5 | 0~32767，精度：1 ，默认：5 | Prevent unexpected results of communication failures.when EMS timeout enabled, watchdog will work and even reading will feed the watchdog,write 0 to disable this function.
328 | 1 | RW | enum16 | EPO enable/disable | EPO使能 | 0-invalid, 1-EPO, 2-DRMO; Default: 0 | 0-无效， 1-EPO功能， 2-DRM0功能， 默认：0 | Enable ONLY when remote Emergency Stop Button is needed
329 | 1 | RW | uint16 | BMS timeout setting | BMS超时时间 | 0~32767，Precision:1，default:5 | 0~32767，精度：1 ，默认：5 | Enable ONLY when remote BMS-inverter connection is needed,write 0 to disable this function.
330 | 1 | RW | enum16 | BMS protocol selection | BMS协议选择 | 0-EP; 1-ALPHA-ESS; 2-PYLONTECH; 3-BMSER; Default：1 | 0-EP， 1-沃太， 2-中兴派能， 3-协能， 默认：1 | 0: energport; 1: alpha; 2: pylontech, only the new version supports BMSER
331 | 1 | RW | enum16 | On-grid/off-grid state default | 默认并离网状态 | 0-on-grid; 1-off-grid； Default:0 | 0-并网； 1-离网, 默认：0
332 | 1 | RW | enum16 | Buzzer enable | 蜂鸣器使能 | 0-disabled, 1- enabled, Default:1 | 0-不使能； 1-使能， 默认：1
333 | 1 | RW | enum16 | Restore factory setting | 恢复出厂设置 | 0-disabled, 1- enabled, Default:0 | 0-不使能； 1-使能， 默认0 | All parameters will be restored to the factory default values, use with caution (only valid for module V208, wall mount V122 and above)
650 | 1 | RW | enum16 | SETDATA_ModOnCmd | 开机 | 1- start, other- invalid | 1- 启动, 其他-无效 | To Start operation, only 1 will be accepted. Reading back value makes no sense
651 | 1 | RW | enum16 | ModOffCmd | 关机 | 1- stop, other- invalid | 1- 停止, 其他-无效 | To Stop operation, only 1 will be accepted. Reading back value makes no sense
652 | 1 | RW | enum16 | ClearFailureCmd | 清除故障 | 1- clear, other- invalid | 1- 清除, 其他-无效 | clear failure flag,when fault occurs, the system will stop and indicates fault. starting is invalid until the fault source is actually removed and this register is written 1. Reading back value makes no sense
653 | 1 | RW | enum16 | OnGridCmd | 并网 | 1- Grid+B151:G151ied,other- invalid | 1- 并网, 其他-无效 | set the module to on grid mode. Reading back value makes no sense
654 | 1 | RW | enum16 | OffGridCmd | 离网 | 1- Off-grid,other- invalid | 1- 离网, 其他-无效 | set the module to off grid mode. Reading back value makes no sense
655 | 1 | RW | enum16 | StandbyCmd | 待机 | 1- Enter Standby, 0- Exit Standby | 0- 退出待机模式, 1- 进入待机模式 | set the module to standby mode,setpoint 0:IGBT switching ,setpoint 1:no IGBT switching,low consumption.let the inverter to halt the IGBT switching, to save the power consumption, but all relays are still closed. Reading back value makes no sense
656 | 1 | RW | enum16 | DC soft start allowing flag | 直流软启允许标志位 | 1-true, other-invalid | 1：是，其它-无效 | DC soft start enable flag bit (only takes effect after the "DC soft start external control enable" bit is enabled)
657 | 1 | RW | enum16 | Machine restart | 整机重启 | 1-true, other-invalid | 1：是，其它-无效 | The whole software restarts after reset
658 | 1 | RW | enum16 | Grid Stop | 电网停机 | 1-true, other-invalid | 1：是，其它-无效
748 | 1 | RW | enum16 | Output voltage level | 输出电压等级 | 0:-380V, 1- 400V, 2- 480V, Default: 1 | 0-380V， 1-400V， 2-480V， 默认：1 | Under 480V, the output voltage level can only be set to 3P3W,Otherwise, report parameter error alarm.
749 | 1 | RW | enum16 | Output frequency level | 输出频率等级 | 0-50Hz, 1-60Hz, Default:0 | 0-50Hz， 1-60Hz， 默认：0 | Internal function, shall not be changed as will
750 | 1 | RW | enum16 | Output voltage system | 输出电压体制 | 0-3P4W, 1-3P3W, Default:1 | 0-3P4W, 1-3P3W ， 默认：1 | Under 480V, the output voltage level can only be set to 3P3W,Otherwise, report parameter error alarm.
752 | 1 | RW | enum16 | Switching device access setting | 切换装置接入设置 | 0-No Switch, 1- Seitch, Default:0 | 0-无切换装置， 1-有切换装置， 默认：0 | connect to ats
753 | 1 | RW | enum16 | Module power level | 模块功率等级 | 0-10kW, 1-20kW, 2-30kW, 3-29kW, Default:2 | 0-10kW, 1-20kW, 2-30kW, 3-29kW， 默认：2 | Internal function, shall not be changed as will
754 | 1 | RW | enum16 | DC voltage level | 直流电压等级 | 0-750V, 1-Invalid, Default:0 | 0-750V， 1-无效， 默认：0 | Not Implemented yet (830V cannot be used)
755 | 1 | RW | enum16 | Model | 机型 | 0-Single CPU, 1-Double CPU, Default:0 | 0-单CPU， 1-双CPU， 默认：0 | 3P3W can only use single CPU
756 | 1 | RW | enum16 | Off-grid and parallel enable | 离网并机使能 | 0-disabled, 1- enabled, Default:0 | 0-不使能, 1-使能, 默认：0
757 | 1 | RW | enum16 | DC soft start external control enable | 直流软启外部控制使能 | 0-disabled, 1- enabled, Default:0 | 0-不使能， 1-使能， 默认：0
768 | 1 | RW | int16 | Grid overvoltage protection I amplitude | 电网过压I段保护幅值 | See the certification supplement page | 见认证参数补充页面
769 | 1 | RW | int16 | ac_ov_trip_time_1 | 电网过压I段保护时间 | See the certification supplement page | 见认证参数补充页面
770 | 1 | RW | int16 | ac_ov_trip_level_2 | 电网过压Ⅱ段保护幅值 | See the certification supplement page | 见认证参数补充页面
771 | 1 | RW | int16 | ac_ov_trip_time_2 | 电网过压Ⅱ段保护时间 | See the certification supplement page | 见认证参数补充页面
772 | 1 | RW | int16 | ac_uv_trip_level_1 | 电网欠压I段保护幅值 | See the certification supplement page | 见认证参数补充页面
773 | 1 | RW | int16 | ac_uv_trip_time_1 | 电网欠压I段保护时间 | See the certification supplement page | 见认证参数补充页面
774 | 1 | RW | int16 | ac_uv_trip_level_2 | 电网欠压Ⅱ段保护幅值 | See the certification supplement page | 见认证参数补充页面
775 | 1 | RW | int16 | ac_uv_trip_time_2 | 电网欠压Ⅱ段保护时间 | See the certification supplement page | 见认证参数补充页面
776 | 1 | RW | int16 | ac_uv_trip_level_3 | 电网欠压Ⅲ段保护幅值 | See the certification supplement page | 见认证参数补充页面
777 | 1 | RW | int16 | ac_uv_trip_time_3 | 电网欠压Ⅲ段保护时间 | See the certification supplement page | 见认证参数补充页面
778 | 1 | RW | int16 | ac_of_trip_level_1 | 电网过频I段保护幅值 | See the certification supplement page | 见认证参数补充页面
779 | 1 | RW | int16 | ac_of_trip_time_1 | 电网过频I段保护时间 | See the certification supplement page | 见认证参数补充页面
780 | 1 | RW | int16 | ac_of_trip_level_2 | 电网过频Ⅱ段保护幅值 | See the certification supplement page | 见认证参数补充页面
781 | 1 | RW | int16 | ac_of_trip_time_2 | 电网过频Ⅱ段保护时间 | See the certification supplement page | 见认证参数补充页面
782 | 1 | RW | int16 | ac_uf_trip_level_1 | 电网欠频I段保护幅值 | See the certification supplement page | 见认证参数补充页面
783 | 1 | RW | int16 | ac_uf_trip_time_1 | 电网欠频I段保护时间 | See the certification supplement page | 见认证参数补充页面
784 | 1 | RW | int16 | ac_uf_trip_level_2 | 电网欠频Ⅱ段保护幅值 | See the certification supplement page | 见认证参数补充页面
785 | 1 | RW | int16 | ac_uf_trip_time_2 | 电网欠频Ⅱ段保护时间 | See the certification supplement page | 见认证参数补充页面
786 | 1 | RW | int16 | reconnect_time | 电网恢复延时 | See the certification supplement page | 见认证参数补充页面
790 | 1 | RW | enum16 | Anti-islanding function | 孤岛检测 | 0-disabled, 1-enabled, Default:1 | 0-禁止使能， 1-使能， 默认：1 | Anti-islanding is a CPUC RULE 21/HECO RULE14H/IEEE1547-requested function to make sure the inverter disconnect from the grid in case of blackout. This is to prevent the formation of an unintended island. The inverter design shall comply with the requirements of IEEE Std 1547 and UL 1741 standards (or latest versions) and be certified to have anti-islanding protection such that the synchronous inverter will automatically disconnect upon a utility system interruption
791 | 1 | RW | enum16 | FVRT function | 频率/电压穿越功能使能 | See the certification supplement page | 见认证参数补充页面 | Frequency and Voltage Ride-Through. The ability to withstand voltage or frequency excursions outside defined limits without tripping or malfunctioning
792 | 1 | RW | enum16 | Reactive power control mode | 无功功率调整模式 | See the certification supplement page | 见认证参数补充页面 | Grid-tied mode only, voltage and frequency setpoint the only setpoints
793 | 1 | RW | enum16 | Power rising mode | 功率变化模式 | See the certification supplement page | 见认证参数补充页面 | To define how the power changes
794 | 1 | RW | enum16 | Active power control mode | 有功功率调整模式 | See the certification supplement page | 见认证参数补充页面 | Grid-tied mode only, Volt/Watt control & Freq/Watt control means active power will be regulated by grid voltage/frequency following a curve/ramp rate given by HECO or CPUC or other local utility authority codes
795 | 1 | RW | enum16 | Grid voltage asymmetric detection | 电网电压不平衡检测使能 | 0-disabled, 1- enabled, Default: See the certification supplement page | 0-不使能,， 1-使能， 默认：见认证参数补充页面 | Grid-tied mode only, voltage and frequency setpoint the only setpoints
796 | 1 | RW | enum16 | continuous overvoltage detection | 连续过压检测使能 | 0-disabled, 1- enabled, Default: See the certification supplement page | 0-不使能， 1-使能， 默认：见认证参数补充页面 | Grid-tied mode only
797 | 1 | RW | enum16 | Grid-existence detection on power-up | 并网开机电网检测使能 | 0-disabled, 1- enabled, Default: See the certification supplement page | 0-不使能,， 1-使能， 默认：见认证参数补充页面 | Grid-tied mode only,detect whether the grid is on-service at powered-up.
798 | 1 | RW | enum16 | Neutral floating detection | 缺N检测使能 | 0-disabled, 1- enabled, default:1 | 0-不使能,，1-使能，默认：1 | Grid-tied mode only
799 | 1 | RW | enum16 | Off-grid black-start mode | 离网启动方式 | 0-normal startup, 1-black startup, Default:0 | 0-正常启动， 1-黑启动， 默认：0 | if disabled, the inverter will start the AC voltage, then close the relay. In some off-grid cases, such as there are inductive loads or transformer, the inrush exciting current will trip the inverter. Enabling this register, the inverter will close the relay first try to limit the current and start the voltage slowly
800 | 1 | RW | enum16 | Grid code selection | 并网认证标准选择 | 0-1741SA, 1-VDE, 2-Australian, 3-G99, 4-Hawaiian, 5-N50549, 6-Austria TypeA, 7-CHN, Default:0 | 0-1741SA， 1-VDE， 2-Australian， 3-G99， 4-Hawaiian， 5-EN50549， 6-Austria TypeA， 7-CHN认证， 默认：0 | Grid-tied mode only, take effect after powering off
801 | 1 | RW | enum16 | Grid-connected active capacity limitation function is enabled | 并网有功容量限制功能使能 | 0-disabled, 1- enabled, Default:0 | 0-不使能， 1-使能， 默认：0
802 | 1 | RW | int16 | Grid active power capacity setting | 并网有功容量设置 | 0~1.0;Precision:0.01,default:0.7 | 0.1~1.0，精度：0.01，默认：0.7
803 | 1 | RW | enum16 | Single phase mode enable and select | 单项模式使能与选择 | 0-dissable, 1- Single phase 230V mode; 2- Single phase 480V mode; fault:0 | 0-不使能， 1-单相230V模式， 2-单相480V模式， 默认0 | Single mode enable and select
804 | 1 | RW | enum16 | Overvoltage drop active enable (only for EN50549 certification) | 过压降有功使能（仅限EN50549认证使用） | See the certification supplement page | 见认证参数补充页面 | Overvoltage drop active enable (only for EN50549 certification)
805 | 1 | RW | enum16 | Start Up Mode | 启动方式 | 0-Manual start, 1-Auto start, Default:0 | 0-手动启动，1-自动启动，默认：0
806 | 1 | RW | enum17 | AC relay detection mode | 交流继电器检测模式 | 0-normal mode, 1-bipolar self-check mode, Default:0 | 0-普通模式，1-双极自检模式，默认为0
807 | 1 | RW | int16 | Local ID number setting | 本机ID号设置 | 1~10; Precision:1; default:1 | 1~10；精度：1；默认：1 | Off-grid and parallel use, 1- is the master, the rest are slaves
808 | 1 | RW | int16 | Float charge voltage | 浮充电压 | 130.0~830.0; Precision: 0.1V; default:130.0 | 130.0~830.0；精度：0.1V；默认：130.0 | When implementing Lithium-ion batteries, these two registers MUST be set to the same
809 | 1 | RW | int16 | Topping charge volage | 恒压充电压 | 130.0~830.0; Precision:0.1V; default:130.0 | 130.0~830.0；精度：0.1V；默认：130.0
810 | 1 | RW | int16 | Current from topping charging to float charging | 恒压充转浮充电流 | 0.0~90.0; Precision:0.1A; default:10.0 | 0.0~90.0；精度：0.1A；默认：10.0 | When implementing Lithium-ion batteries,this register MUST be set to 0
811 | 1 | RW | int16 | Max charging current | 最大充电电流 | 0.0~90.0; Precision:0.1A; default:90.0 | 0.0~90.0；精度：0.1A；默认：90.0 | Limit the max DC currents, keep default if you don't need to (Do not write EEPROM)
812 | 1 | RW | int16 | Max discharging current | 最大放电电流 | 0.0~90.0; Precision:0.1A; default:90.0 | 0.0~90.0；精度：0.1A；默认：90.0 | Limit the min DC currents, keep default if you don't need to (Do not write EEPROM)
813 | 1 | RW | int16 | Lower voltage limit of battery protection | 电池电压下限保护阈值 | 130.0~830.0; Precision:0.1V; default:130.0 | 130.0~830.0；精度：0.1V；默认：130.0
814 | 1 | RW | int16 | Upper voltage limit of battery protection | 电池电压上限保护阈值 | 130.0~830.0; Precision:0.1V; default:130.0 | 130.0~830.0；Precision：0.1V；默认：130.0 | This register can't be set lower than 0x0328 and 0x0329
815 | 1 | RW | uint16 | Battery voltage protection limit back the difference | 电池电压保护下限回差值 | 5.0~80; Precision:0.1V; default:20.0 | 5.0~80；精度：0.1V；默认：20.0
825 | 1 | RW | enum16 | Leakage current DC component detector enable | 漏电流直流分量检测使能 | 0-disabled, 1- enabled, Default:0 | 0-不使能， 1-使能， 默认：0 | /
846 | 1 | RW | int16 | Resume and limit the frequency online | 恢复并网上限频率 | 0.1～1; Precision:0.01Hz; default:0.10 | 0.1～1；精度：0.01Hz；默认：0.10
847 | 1 | RW | int16 | Restore the lower frequency of grid connection | 恢复并网下限频率 | -1.00～-0.10; Precision:0.01Hz; default:-0.10 | -1.00～-0.10；精度：0.01Hz；默认：-0.10
848 | 1 | RW | uint16 | Voltage Reactive Reference Voltage Vref | 电压无功调节参考电压Vref | See the certification supplement page | 见认证参数补充页面
849 | 1 | RW | uint16 | Voltage and reactive power adjustment point V1 | 电压无功调节点V1 | See the certification supplement page | 见认证参数补充页面
850 | 1 | RW | int16 | Volt-VAr: V2, Voltage setpoint @ Q2 | 电压调无功: 调节点V2 | See the certification supplement page | 见认证参数补充页面 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var.
851 | 1 | RW | int16 | Volt-VAr: V3, Voltage setpoint @ Q3 | 电压调无功: 调节点V3 | See the certification supplement page | 见认证参数补充页面 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var.
852 | 1 | RW | int16 | Volt-VAr: V4, Voltage setpoint @ Q4 | 电压调无功: 调节点V4 | See the certification supplement page | 见认证参数补充页面 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var.
853 | 1 | RW | int16 | Volt-VAr: Q1, Max capacitive reactive regulation | 电压调无功:最大容性无功调节量Q1 | See the certification supplement page | 见认证参数补充页面 | ratio * rated power, Available only when reactive power regulation mode is set to Volt/Var.
854 | 1 | RW | int16 | Volt-VAr: Q2, Initial capacitive reactive regulation | 电压调无功:初始容性无功调节量Q2 | See the certification supplement page | 见认证参数补充页面 | ratio * rated power, Available only when reactive power regulation mode is set to Volt/Var.
855 | 1 | RW | int16 | Volt-VAr: Q3, Initial inductive reactive regulation | 电压调无功:初始感性无功调节量Q3 | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
856 | 1 | RW | int16 | Volt-VAr: Q4, Max inductive reactive regulation | 电压调无功:最大感性无功调节量Q4 | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
857 | 1 | RW | int16 | Volt-VAr: response time | 电压调无功:调节反应时间 | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
858 | 1 | RW | int16 | Reactive first order response time (VDE authentication only) | 无功一阶响应时间（仅用于VDE认证） | See the certification supplement page | 见认证参数补充页面
862 | 1 | RW | int16 | Volt-Watt: initial voltage Vstart | 过压降有功起始调节点Vstart | See the certification supplement page | 见认证参数补充页面 | ratio * rated voltage, Available only when active power regulation mode is set to Volt/Watt and operating in discharge mode, follow the FVRT table given by HECO or CPUC or other local utility authority codes.
863 | 1 | RW | int16 | Volt-Watt: end voltage Vstop | 过压降有功终止调节点Vstop | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
864 | 1 | RW | int16 | Volt-Watt: initial power Pstart | 过压降有功起始功率Pstart | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
865 | 1 | RW | int16 | Volt-Watt: end power Pstop | 过压降有功终止功率Pstop | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
866 | 1 | RW | int16 | Volt-Watt: return to service delay | 过压降有功恢复延时 | See the certification supplement page | 见认证参数补充页面 | To set the output power recovery time delay after the utility voltage returns to normal
867 | 1 | RW | int16 | Volt-Watt: response time | 过压降有功反应时间 | See the certification supplement page | 见认证参数补充页面 | refer to HECO RULE 14, keep default value if no aware of it
868 | 1 | RW | int16 | Freq-Watt(Discharge): start of frequency drop | 放电过频降有功起始点 | See the certification supplement page | 见认证参数补充页面 | Available only when active power regulation mode is set to Freq/Watt and operating in discharge mode. When the actual frequency is above the point, the active power will be regulated(lowered) with the ramp rate In Australia, this register shall be fixed to 0.25Hz
869 | 1 | RW | int16 | Freq-Watt (Discharge): slope of frequency drop | 放电过频降有功调节斜率 | See the certification supplement page | 见认证参数补充页面 | The ramp rate is defined as multiple of set active power per hertz that above the above the Freq/Watt regulation point. Available only when active power regulation mode is set to Freq/Watt and operating in discharge mode. Example: Rated frequency is 60Hz, the target active power is set to 10kW, Freq/Watt regulation point is set to 2Hz, ramp rate is set as 0.5, If the actual frequency reaches 63Hz, the output active power will be 10kW-(63Hz-62Hz)×0.5*(10kW/Hz) = 5kW
870 | 1 | RW | int16 | Freq-Watt (Discharge) (Australia only): Fstop-DISCH | 放电过频降有功终点（用于澳洲认证） | See the certification supplement page | 见认证参数补充页面 | AS4777 only, bias Bias from rated frequency
871 | 1 | RW | int16 | Freq-Watt(Charge)(Australia only): Fstop-CH | 充电欠频降有功终点（用于澳洲认证） | See the certification supplement page | 见认证参数补充页面 | AS4777 only, bias Bias from rated frequency
872 | 1 | RW | int16 | Volt-Watt (Charge)(Australia only) : Vstart-CH | 充电欠压降有功起始点（用于澳洲认证） | See the certification supplement page | 见认证参数补充页面 | %Vrated,AS4777 only, ratio
876 | 1 | RW | int16 | Soft-start Ramp Rate(SS) | 软启功率变化速率 | See the certification supplement page | 见认证参数补充页面 | SS takes effect when the inverter starts, or when the inverter is on "grid reconnection" after the trip caused by FVRT timeout
877 | 1 | RW | int16 | Power Ramp Rate(RR) | 功率变化速率 | See the certification supplement page | 见认证参数补充页面 | RR takes effect in Volt-Watt or Freq-Watt mode when the grid is back to normal state and the inverter tring to go back to normal output. In other words, as long as the inverter doesn’t trip, and the inverter had derated the output power, RR takes effect when the inverter tries to go back to normal output. Available only when Power rising mode is set to ramp mode. If the value is 2.000, which means within 0.5 seconds the system can runs to full power output.
878 | 1 | RW | int16 | Power factor setting | 功率因数设置 | -1~+1, Precision: 0.01, default: 1; | -1~+1；精度： 0.01；默认：1; | Available only when Constant PF is enabled,Negative inductive, positive capacitive (Do not write EEPROM)
879 | 1 | RW | int16 | Watt-PF: P1 | 有功调节功率因数: 有功调节点P1 | See the certification supplement page | 见认证参数补充页面 | Available only when active power regulation mode is set to Freq/Watt and operating in discharge mode. When the actual frequency is above the point, the active power will be regulated(lowered) with the ramp rate
880 | 1 | RW | int16 | Watt-PF: P2 | 有功调节功率因数: 有功调节点P2 | See the certification supplement page | 见认证参数补充页面 | %Prated
881 | 1 | RW | int16 | Watt-PF: P3 | 有功调节功率因数: 有功调节点P3 | See the certification supplement page | 见认证参数补充页面 | %Prated
882 | 1 | RW | int16 | Watt-PF: P4 | 有功调节功率因数: 有功调节点P4 | See the certification supplement page | 见认证参数补充页面 | %Prated
883 | 1 | RW | int16 | Watt-PF: PF1 | 有功调节功率因数: 功率因数调节点PF1 | See the certification supplement page | 见认证参数补充页面 | +(lagging), -(leading),
884 | 1 | RW | int16 | Watt-PF: PF2 | 有功调节功率因数: 功率因数调节点PF2 | See the certification supplement page | 见认证参数补充页面 | +(lagging), -(leading),
885 | 1 | RW | int16 | Watt-PF: PF3 | 有功调节功率因数: 功率因数调节点PF3 | See the certification supplement page | 见认证参数补充页面 | +(lagging), -(leading),
886 | 1 | RW | int16 | Watt-PF: PF4 | 有功调节功率因数: 功率因数调节点PF4 | See the certification supplement page | 见认证参数补充页面 | +(lagging), -(leading),
887 | 1 | RW | int16 | continous over voltage trip threshold in 10 minutes | 10分钟连续过压保护幅值 | See the certification supplement page | 见认证参数补充页面
888 | 1 | RW | int16 | frequency variation rate trip threshold | 电网频率变化率超额保护阈值 | 0:disabled, 1: rate limit 0.125Hz/s, 2: rate limit 0.2Hz/s, Default:See the certification supplement page | 0：不使能 ， 1：变化率限值为0.125Hz/s， 2：变化率限值为0.2Hz/s， 默认：见认证参数补充页面
889 | 1 | RW | int16 | Phase angle abrupt trip threshold | 电网相角突变保护阈值 | 0:disabled, 1:angle abrupt limit 12°, 2:angle abrupt limit 6°, Default：See the certification supplement page | 0:不使能， 1:角度突变限值为12度， 2:角度突变限值为6度， 默认：见认证参数补充页面
890 | 1 | RW | int16 | Grid Reconnection: voltage upper limit | 电网重连上限电压 | See the certification supplement page | 见认证参数补充页面 | Available only when Power rising mode is set to ramp mode . once tripped after FVRT timeout, the inverter can reconnect to the grid when frequency or voltage is back to the thresholds defined as "grid is back to service". In HECO14 /CPUC 21, this register is unnecessary to
891 | 1 | RW | int16 | Grid Reconnection: voltage lower limit | 电网重连下限电压 | See the certification supplement page | 见认证参数补充页面
892 | 1 | RW | int16 | Grid Reconnection: frequency upper limit | 电网重连上限频率 | See the certification supplement page | 见认证参数补充页面 | Available only when Power rising mode is set to ramp mode once tripped after FVRT timeout, the inverter can reconnect to the grid when frequency or voltage is back to the thresholds defined as "grid is back to service"
893 | 1 | RW | int16 | Grid Reconnection: frequency lower limit | 电网重连下限频率 | See the certification supplement page | 见认证参数补充页面 | Bias from rated frequency
894 | 1 | RW | int16 | Freq-Watt ramp rate(low freq)(Only for VDE) | 欠频有功调节斜率（仅VDE用） | See the certification supplement page | 见认证参数补充页面
934 | 1 | RO | int16 | Analog_ ActivePower_3Phase(Meter) | 总有功功率(电表) | 0.01kW | 0.01kW | Meter options
948 | 1 | RW | uint16 | PhA grid voltage calibration parameters | A相电网电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001；默认：1
949 | 1 | RW | uint16 | PhB grid voltage calibration parameters | B相电网电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
950 | 1 | RW | uint16 | PhC grid voltage calibration parameters | C相电网电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
951 | 1 | RW | uint16 | PhA inverter voltage calibration parameters | A相逆变电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
952 | 1 | RW | uint16 | PhA inverter voltage calibration parameters | B相逆变电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
953 | 1 | RW | uint16 | PhA inverter voltage calibration parameters | C相逆变电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
954 | 1 | RW | uint16 | PhA inductor current calibration parameters 1 | A相电感电流校准参数1 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
955 | 1 | RW | uint16 | PhB inductor current calibration parameters 1 | B相电感电流校准参数1 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
956 | 1 | RW | uint16 | PhC inductor current calibration parameters 1 | C相电感电流校准参数1 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
957 | 1 | RW | uint16 | PhA inductor current calibration parameters 2 | A相电感电流校准参数2 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
958 | 1 | RW | uint16 | PhB inductor current calibration parameters 2 | B相电感电流校准参数2 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
959 | 1 | RW | uint16 | PhC inductor current calibration parameters 2 | C相电感电流校准参数2 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
960 | 1 | RW | uint16 | PhA output current calibration parameters | A相输出电流校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
961 | 1 | RW | uint16 | PhB output current calibration parameters | B相输出电流校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
962 | 1 | RW | uint16 | PhC output current calibration parameters | C相输出电流校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
963 | 1 | RW | uint16 | Positive bus voltage calibration parameters | 正母线电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
964 | 1 | RW | uint16 | Negative bus voltage calibration parameters | 负母线电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
965 | 1 | RW | uint16 | DC voltage calibration parameters | 直流电压校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
966 | 1 | RW | uint16 | DC current calibration parameters | 直流电流校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
967 | 1 | RW | uint16 | DC inductor current calibration parameters | 直流电感电流校准参数 | 0.900~1.100,Precision:0.001,default:1 | 0.900~1.100，精度：0.001，默认：1
4001 | 6 | W | uint16 | Time setting - Year\Month\Day\Hour\Minute\Second | 设置时间：年\月\日\时\分\秒 | YYYYMMDDHHmmss | eg:21.01.02 - 15.25.30 | YYYYMMDDHHmmss，Only need to write the lower 8 digits for the year
4007 | 2 | W | acc32 | password | 高级密码 | acc32 | acc32 | Password needed to unlock factory modes, invalid in 90s

## certification supplement page
Address | Register Name 寄存器名称 | Define | 1741SA | 欧洲 (VDE) | 澳洲(Australian) | 英国 (G99) | 夏威夷(Hawaiian) | 欧洲(EN50549) | 奥地利typeA (Austria TypeA) | 中国 (CHN)
768 | Over-volt region 1 boundary 过压I段保护范围 | 1.05~1.25, Precision: 0.01(*Vnom) | 110 | 125 | 113 | 114 | 110 | 120 | 115 | 110
769 | Over-volt region 1 trip time 过压I段保护时间 | 0.00~100.00, Precision: 0.01s | 1300 | 10 | 150 | 100 | 100 | 500 | 10 | 100
770 | Over-volt region 2 boundary 过压II段保护范围 | 1.05~1.30, Precision: 0.01(*Vnom) | 120 | 125 | 115 | 119 | 120 | 125 | 115 | 120
771 | Over-volt region 2 trip time 过压II段保护时间 | 0.00~5.00, Precision: 0.01s | 16 | 10 | 10 | 50 | 16 | 10 | 10 | 10
772 | Under-volt region 1 boundary 欠压I段保护范围 | 0.20~0.95, Precision: 0.01(*Vnom) | 92 | 80 | 78 | 87 | 88 | 80 | 80 | 85
773 | Under-volt region 1 trip time 欠压I段保护时间 | 0.00~100.00, Precision: 0.01s | 2100 | 300 | 150 | 250 | 2100 | 300 | 150 | 100
774 | Under-volt region 2 boundary 欠压II段保护范围 | 0.20~0.95, Precision: 0.01(*Vnom) | 70 | 45 | 78 | 80 | 70 | 40 | 25 | 50
775 | Under-volt region 2 trip time 欠压II段保护时间 | 0.00~50.00, Precision: 0.01s | 1100 | 10 | 150 | 50 | 1100 | 150 | 50 | 10
776 | Under-volt region 3 boundary 欠压III段保护范围 | 0.20~0.95, Precision: 0.01(*Vnom) | 50 | 45 | 78 | 80 | 50 | 40 | 25 | 50
777 | Under-volt region 3 trip time 欠压III段保护时间 | 0.00~21.00, Precision: 0.01s | 150 | 10 | 150 | 50 | 200 | 150 | 50 | 10
778 | Over-freq region 1 boundary 过频I段保护范围 | 0.00~6.00Hz, Precision: 0.01(+Fnom) | 50 | 150 | 200 | 150 | 300 | 150 | 150 | 20
779 | Over-freq region 1 trip time 过频I段保护时间 | 0.0~1000.0, Precision: 0.1s | 3000 | 1 | 1 | 900 | 210 | 5 | 1 | 1
780 | Over-freq region 2 boundary 过频II段保护范围 | 0.00~6.00Hz, Precision: 0.01(+Fnom) | 200 | 150 | 200 | 200 | 500 | 200 | 150 | 50
781 | Over-freq region 2 trip time 过频II段保护时间 | 0.0~1000.0, Precision: 0.1s | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
782 | Under-freq region 1 boundary 欠频I段保护范围 | -10.00 ~ 0.00Hz, Precision: 0.01(+Fnom) | -150 | -250 | -300 | -250 | -300 | -250 | -250 | -50
783 | Under-freq region 1 trip time 欠频I段保护时间 | 0.0~1000.0, Precision: 0.1s | 3000 | 1 | 15 | 200 | 210 | 5 | 1 | 1
784 | Under-freq region 2 boundary 欠频II段保护范围 | -10 ~ 0.00Hz, Precision: 0.01(+Fnom) | -300 | -250 | -300 | -300 | -1000 | -300 | -250 | -200
785 | Under-freq region 2 trip time 欠频II段保护时间 | 0.0~1000.0, Precision: 0.1s | 1 | 1 | 15 | 5 | 1 | 1 | 1 | 1
786 | Grid reconnection delay 电网恢复延时 | 35~600, Precision: 1s | 300 | 35 | 35 | 50 | 300 | 35 | 300 | 35
791 | FVRT function Enable 电压频率穿越功能使能 | 0- disable, 1- enable | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
792 | Reactive power control mode 无功控制模式 | 0: Constant reactive power 1: Volt-VAr enabled 2: Constant PF 3: Watt-PF enabled (VDE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
793 | Power change mode 功率变化模式 | 0- Step, 1- Ramp | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0
794 | Active power control mode 有功控制模式 | 0: Constant Active power 1: Volt-Watt enabled 2: Freq-Watt enabled 3: Volt-Watt + Freq-Watt enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
795 | Grid voltage unbalance detection enable 电网电压不平衡检测使能 | 0-disabled,1- enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
796 | Continuous overvoltage detection enable 连续过压检测使能 | 0-disabled,1- enabled | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0
797 | Grid-connected power-on grid detection enable 并网开机电网检测使能 | 0-disabled,1- enabled | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0
800 | Grid-connected certification standard selection 并网认证标准选择 | 0-1741SA, 1-VDE, 2-Australian, 3-G99, 4-Hawaiian, 5-EN50549, 6-Austria TypeA, 7-CHN | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
801 | 并网有功容量限制功能使能 | Grid-connected active capacity limitation function is enabled | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802 | 并网有功容量设置 | Grid active power capacity setting | 100 | 70 | 100 | 100 | 100 | 100 | 100 | 100
804 | 过压降有功使能（804寄存器，仅限EN50549认证使用） | 0-disabled,1- enabled | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
848 | Volt-VAr Vref 电压无功调节参考电压 | 0.950~1.050, Precision: 0.001(*Vnom) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
849 | Volt-VAr V1 电压无功调节点V1 | 0.820~1.030, Precision: 0.001(*Vnom) | 920 | 930 | 900 | 920 | 940 | 930 | 920 | 920
850 | Volt-VAr V2 电压无功调节点V2 | 0.900~1.050, Precision: 0.001(*Vnom) | 980 | 970 | 957 | 980 | 970 | 970 | 960 | 980
851 | Volt-VAr V3 电压无功调节点V3 | 0.950~1.150, Precision: 0.001(*Vnom) | 1020 | 1030 | 1087 | 1020 | 1030 | 1030 | 1050 | 1020
852 | Volt-VAr V4 电压无功调节点V4 | 0.970~1.180, Precision: 0.001(*Vnom) | 1060 | 1070 | 1150 | 1060 | 1060 | 1070 | 1080 | 1060
853 | Maximum capacitive reactive Q1 最大容性无功调节量Q1 | 0.00 ~ 0.60, Precision: 0.01(*Pnom), +(leading), -(lagging) | 30 | 48 | 30 | 30 | 44 | 48 | 48 | 30
854 | Initial capacitive reactive Q2 初始容性调节量Q2 | 0.00 ~ 0.60, Precision: 0.01(*Pnom), +(leading), -(lagging) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
855 | Initial inductive reactive Q3 初始感性调节量Q3 | 0.00 ~ 0.60, Precision: 0.01(*Pnom), +(leading), -(lagging) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
856 | Maximum inductive reactive Q4 最大感性调节量Q4 | 0.00 ~ 0.60, Precision: 0.01(*Pnom), +(leading), -(lagging) | 30 | 48 | 30 | 30 | 44 | 48 | 48 | 30
857 | Volt-VAr response time 电压无功调节反应时间 | 0.00~90.00, Precision: 0.01s | 1000 | 0 | 0 | 0 | 1000 | 0 | 0 | 1000
858 | 无功一阶响应时间（仅VDE认证） Reactive first order response time(only VDE) | 6~60, Precision: 1s | invalid | 10 | invalid | invalid | invalid | 10 | 15 | invalid
862 | Volt-Watt start V1(high volt) 过压有功调节起始点V1 | 1.010~1.200, Precision: 0.001(*Vnom) | 1060 | 1060 | 1087 | 1060 | 1060 | 1060 | 1100 | 1060
863 | Over-Volt-Watt end V2(high volt) 过压有功调节终止点V2 | 1.020~1.200, Precision: 0.001(*Vnom) | 1100 | 1100 | 1150 | 1100 | 1100 | 1100 | 1120 | 1100
864 | Over-Volt-Watt start P1(high volt) 过压有功调节起始功率P1 | 0.00~1.00, Precision: 0.01(*Pset) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
865 | Over-Volt-Watt end P2(high volt) 过压有功调节终止功率P2 | 0.00~1.00, Precision: 0.01(*Pset) | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
866 | Over-Vol-Watt delay(high volt) 过压有功调节恢复延时 | 3.00~90.00, Precision: 0.01s | 6000 | 6000 | 0 | 6000 | 6000 | 6000 | 0 | 6000
867 | Over-Volt-Watt response time(high volt) 过压有功调节反应时间 | 0.50~60.00, Precision: 0.01s | 1000 | 1000 | 0 | 1000 | 1000 | 1000 | 0 | 1000
868 | Over-Freq-Watt start freq point 过频有功调节起始点 | 0.10~1.00, Precision: 0.01(*Fnom) | 10 | 20 | 底层写死 | 10 | 4 | 20 | 20 | 10
869 | Over-Freq-Watt ramp rate 过频有功调节斜率 | 0.02~0.12, Precision: 0.01 | 5 | 5 | invalid | 5 | 42 | 5 | 5 | 5
870 | Over-Freq-Watt end freq point 过频有功调节终止点 | 0.26~3.00, Precision: 0.01(*Fnom) | invalid | invalid | 200 | invalid | invalid | invalid | invalid | invalid
871 | Under-Freq-Watt start freq point 欠频有功调节终止点 | -4.00 ~ -0.26, Precision: 0.01(*Fnom) | invalid | invalid | -100 | invalid | invalid | invalid | invalid | invalid
872 | Under-Freq-Watt start freq point 欠压有功调节起始点 | 0.900~1.000, Precision: 0.001(*Vnom) | invalid | invalid | 957 | invalid | invalid | invalid | invalid | invalid
876 | SS-Soft-start ramp rate 软启动功率变化速率 | 0.0010~3.0000, Precision: 0.0001(*Pnom/s) | 200 | 16 | 27 | 30000 | 33 | 16 | 16 | 30000
877 | RR-Normal ramp rate 常规功率变化速率 | 0.0010~3.0000, Precision: 0.0001(*Pnom/s) | 30000 | 65 | 30000 | 30000 | 30000 | 65 | 65 | 30000
879 | PF curve mode P1 PF曲线模式功率调节点P1 | 0.20~1.00, Precision: 0.01(*Pnom) | 20 | 50 | 25 | 20 | 20 | 25 | 25 | 20
880 | PF curve mode P2 PF曲线模式功率调节点P2 | 0.20~1.00, Precision: 0.01(*Pnom) | 50 | 50 | 50 | 50 | 50 | 40 | 50 | 50
881 | PF curve mode P3 PF曲线模式功率调节点P3 | 0.20~1.00, Precision: 0.01(*Pnom) | 70 | 50 | 75 | 70 | 70 | 60 | 75 | 70
882 | PF curve mode P4 PF曲线模式功率调节点P4 | 0.20~1.00, Precision: 0.01(*Pnom) | 100 | 100 | 100 | 100 | 100 | 75 | 100 | 100
883 | PF curve mode PF1 PF曲线模式功率调节点PF1 | -0.90~ -1.00, 0.90~1.00, Precision: 0.01, +(leading), -(lagging) | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100
884 | PF curve mode PF2 PF曲线模式功率调节点PF2 | -0.90~ -1.00, 0.90~1.00, Precision: 0.01, +(leading), -(lagging) | 100 | 100 | 100 | 100 | 100 | 98 | 100 | 100
885 | PF curve mode PF3 PF曲线模式功率调节点PF3 | -0.90~ -1.00, 0.90~1.00, Precision: 0.01, +(leading), -(lagging) | 96 | 100 | 97 | 96 | 96 | -98 | 95 | 96
886 | PF curve mode PF4 PF曲线模式功率调节点PF4 | -0.90~ -1.00, 0.90~1.00, Precision: 0.01, +(leading), -(lagging) | 90 | 90 | 95 | 90 | 90 | -90 | 90 | 90
887 | Over-volt for 10 minutes 10分钟过压幅值 | 1.06~1.12, Precision: 0.01(*Vnom) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
888 | frequency variation rate trip threshold 电网频率变化率超额保护阈值 | 0:disabled 1: rate limit 0.125Hz/s 2: rate limit 0.2Hz/s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
889 | Phase angle abrupt trip threshold电网相角突变保护阈值 | 0:disabled, 1:angle abrupt limit 12°, 2:angle abrupt limit 6°. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
890 | Grid reconnection upper limit volt 电网重连上限电压 | 1.000~1.150, Precision: 0.001(*Vnom) | 1050 | 1100 | 1104 | 1123 | 1100 | 1100 | 1090 | 1100
891 | Grid reconnection lower limit volt 电网重连下限电压 | 0.800~1.000, Precision: 0.001(*Vnom) | 920 | 850 | 887 | 870 | 850 | 850 | 850 | 850
892 | Grid reconnection upper limit freq 电网重连上限频率 | 0.00~3.00, Precision: 0.01(+Fnom) | 10 | 50 | 10 | 100 | 5 | 10 | 10 | 5
893 | Grid reconnection lower limit freq 电网重连下限频率 | -3.00 ~ -0.00, Precision: 0.01(+Fnom) | -50 | -250 | -250 | -240 | -250 | -250 | -250 | -250
894 | Under-Freq-Watt ramp rate(low freq) 欠频有功调节斜率 | 0.02~0.12, Precision: 0.01 | invalid | 5 | invalid | invalid | invalid | 5 | invalid | invalid

## SUNSPEC_PROTOCOL (hidden)
Address | Size | Access | Type | Register Name | 寄存器名称 | Unit | 单位 | Comments Function Code: 0x03(R)\0x06(W)
41 | Bit0 | RO | bitfield | Output ground fault | 输出接地故障 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit1 | RO | bitfield | DC overvoltage | 直流过电压 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit2 | RO | bitfield | AC relay disconnected | 交流继电器断开 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit3 | RO | bitfield | DC disconnect | 直流断开 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit4 | RO | bitfield | Grid off | 电网关闭 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit5 | RO | bitfield | Cabinet open | 柜开 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit6 | RO | bitfield | Manual shutdown | 手动关机 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit7 | RO | bitfield | Overtemperature | 过温 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit8 | RO | bitfield | AC over frequency | 交流过频 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit9 | RO | bitfield | AC underfrequency | 交流欠频 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit10 | RO | bitfield | AC voltage exceeds the upper limit | 交流电压超过上限 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit11 | RO | bitfield | AC voltage exceeds the lower limit | 交流电压超过下限 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit12 | RO | bitfield | Blowing string fuse input | 吹串式保险丝输入 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit13 | RO | bitfield | The temperature is too low | 温度过低 | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit14 | RO | bitfield | General memory or communication error (internal) | 通用内存或通讯错误（内部） | 1- Fault，0- Normal | 1- 故障，0- 正常
41 | Bit15 | RO | bitfield | Failed hardware test | 硬件测试失败 | 1- Fault，0- Normal | 1- 故障，0- 正常
500 | 2 | RO | uint32x | SunSpec_ID | 知名价值。唯一标识这是一个SunSpec Modbus Map |  | / | Well-known value. Uniquely identifies this as a SunSpec Modbus Map
502 | 1 | RO | uint16 | SunSpec_DID_0001 | 唯一标识这是一个SunSpec公共模型块 |  | / | Uniquely identifies this as a SunSpec Common Model Block
503 | 1 | RO | uint16 | SunSpec_Length_0001 | 16位寄存器中的块长度 |  | / | Length of block in 16-bit registers
504 | 16 | RO | string | Manufacturer | 制造商序列号 |  | / | Manufacturer
520 | 16 | RO | string | Model | 制造商特定值（32个字符） |  | / | Manufacturer specific value (32 chars)
536 | 8 | RO | string | Options | 制造商特定值（16个字符） |  | / | Baud rate + data bit + stop bit + parity bit
544 | 8 | RO | string | Version | 制造商特定值（16 chars） |  | / | Manufacturer specific value (16 chars)
552 | 16 | RO | string | Serial Number | 制造商特定值（32个字符） |  | / | Manufacturer specific value (32 chars)
568 | 1 | RW | uint16 | Device Address | Modbus设备地址 |  | / | Modbus device address
569 | 1 | RO | pad | pad | 强制均匀对齐 |  | / | Force even alignment
570 | 1 | RO | uint16 | SunSpec_DID_0103 | 103 - 三相逆变器 |  | / | 103 - 3-phase inverter
571 | 1 | RO | uint16 | SunSpec_Length_0103 | 模型块在寄存器中的长度 |  | / | Length of model block in registers
572 | 1 | RO | uint16 | Amps | 交流电流 |  | A | AC Current
573 | 1 | RO | uint16 | Amps PhaseA | A相电流 |  | A | Phase A Current
574 | 1 | RO | uint16 | Amps PhaseB | B相电流 |  | A | Phase B Current
575 | 1 | RO | uint16 | Amps PhaseC | C相电流 |  | A | Phase C Current
576 | 1 | RO | sunssf | A_SF | 交流电流​​比例系数 |  | SF | AC Current Scale factor
577 | 1 | RO | uint16 | PPVphAB | AB线电压 |  | V | Phase Voltage AB
578 | 1 | RO | uint16 | PPVphBC | BC线电压 |  | V | Phase Voltage BC
579 | 1 | RO | uint16 | PPVphCA | CA线电压 |  | V | Phase Voltage CA
580 | 1 | RO | uint16 | PhVphA | A相电压 |  | V | Phase Voltage AN
581 | 1 | RO | uint16 | PhVphB | B相电压 |  | V | Phase Voltage BN
582 | 1 | RO | uint16 | PhVphC | C相电压 |  | V | Phase Voltage CN
583 | 1 | RO | sunssf | V_SF | 交流电压比例系数 |  | SF | AC Voltage Scale factor
584 | 1 | RO | int16 | Watts | 交流功率 |  | W | AC Power
585 | 1 | RO | sunssf | W_SF | 交流功率比例系数 |  | SF | AC Power Scale factor
586 | 1 | RO | uint16 | Hz | 线路频率 |  | Hz | Line Frequency
587 | 1 | RO | sunssf | Hz_SF | 比例系数 |  | SF | Scale factor
588 | 1 | RO | int16 | VA | 交流视在功率 |  | VA | AC Apparent Power
589 | 1 | RO | sunssf | VA_SF | 比例系数 |  | SF | Scale factor
590 | 1 | RO | int16 | Var | 交流无功功率 |  | var | AC Reactive Power
591 | 1 | RO | sunssf | VAr_SF | 比例系数 |  | SF | Scale factor
592 | 1 | RO | int16 | PF | 交流功率因数 |  | Pct | AC Power Factor
593 | 1 | RO | sunssf | PF_SF | 比例系数 |  | SF | Scale factor
594 | 2 | RO | acc32 | WattHours | 交流能量 |  | Wh | AC Energy
596 | 1 | RO | sunssf | WH_SF | 比例系数 |  | SF | Scale factor
597 | 1 | RO | uint16 | DC Amps | 直流电流 |  | A | DC Current
598 | 1 | RO | sunssf | DCA_SF | 比例系数 |  | SF | Scale factor
599 | 1 | RO | uint16 | DC Voltage | 直流电压 |  | V | DC Voltage
600 | 1 | RO | sunssf | DCV_SF | 比例系数 |  | SF | Scale factor
601 | 1 | RO | int16 | DC Watts | 直流功率 |  | W | DC Power
602 | 1 | RO | sunssf | DCW_SF | 比例系数 |  | SF | Scale factor
603 | 1 | RO | int16 | Cabinet Temperature | 机柜温度 |  | C | Cabinet Temperature
604 | 1 | RO | int16 | Heat Sink Temperature | 散热器温度 |  | C | Heat Sink Temperature | DCAC circuit heat sink
605 | 1 | RO | int16 | Transformer Temperature | 变压器温度 |  | C | Transformer Temperature | No transformer
606 | 1 | RO | int16 | Other Temperature | 其他温度 |  | C | Other Temperature | DCDC circuit heat sink
607 | 1 | RO | sunssf | Tmp_SF | 温度比例系数 |  | SF | Scale factor
608 | 1 | RO | enum16 | Operating State | 枚举值。工作状态 |  | / | Enumerated value. Operating state | report the current operating status of the inverter
609 | 1 | RO | enum16 | Vendor Operating State | 操作状态代码 |  | / | Vendor specific operating state code,reversed
610 | 2 | RO | bitfield32 | Event1 | 位阈事件 |  | / | Bitmask value. Event fields
612 | 2 | RO | bitfield32 | Event Bitfield 2 | Faults 95:64 occured |  | / | Vendor defined events | Faults 95:64 occured
614 | 2 | RO | bitfield32 | Vendor Event Bitfield 1 | Faults 127:96 occured |  | / | reversed | Faults 127:96 occured
616 | 2 | RO | bitfield32 | Vendor Event Bitfield 2 | Faults 159:128 occurred |  | / | reversed | Faults 159:128 occurred
618 | 2 | RO | bitfield32 | Vendor Event Bitfield 3 | Faults 191:160 occured |  | / | reversed | Faults 191:160 occured
620 | 2 | RO | bitfield32 | Vendor Event Bitfield 4 | Faults 223:192 occured |  | / | reversed | Faults 223:192 occured
622 | 1 | RO | uint16 | SunSpec_DID_FFFF | SunSpec终止块 |  | / | SunSpec End Block
623 | 1 | RO | uint16 | SunSpec_Length_FFFF | 结束块的长度 |  | / | Length of End Block
0x0260 （608）Operation enum16 list
enum16 | St |  |  |  | OFF | 关机 | 1
enum16 | St |  |  |  | SLEEPING (NOT implemented yet) | 睡眠（未启用） | 2
enum16 | St |  |  |  | STARTING (NOT implemented yet) | 开机中 | 3
enum16 | St |  |  |  | MPPT (NOT implemented yet) | MPPT（未启用） | 4
enum16 | St |  |  |  | THROTTLED | 限流 | 5
enum16 | St |  |  |  | SHUTTING_DOWN (NOT implemented yet) | 关机中 | 6
enum16 | St |  |  |  | FAULT | 故障 | 7
enum16 | St |  |  |  | STANDBY | 待机 | 8
enum16 | St |  |  |  | STARTED | 已启动 | 9
0x0262（610） Event bitfield32 list
bitfield32 | Evt1 |  |  |  | GROUND_FAULT | 接地故障 | bit0
bitfield32 | Evt1 |  |  |  | DC_OVER_VOLT | 直流侧过压 | bit1
bitfield32 | Evt1 |  |  |  | AC_DISCONNECT(AC relays open) | AC继电器断开 | bit2
bitfield32 | Evt1 |  |  |  | DC_DISCONNECT(DC relays open) | DC继电器断开 | bit3
bitfield32 | Evt1 |  |  |  | GRID_DISCONNECT | 电网断开 | bit4
bitfield32 | Evt1 |  |  |  | CABINET_OPEN (NOT implemented yet) | 机柜打开（未启用） | bit5
bitfield32 | Evt1 |  |  |  | MANUAL_SHUTDOWN | 手动关机 | bit6
bitfield32 | Evt1 |  |  |  | OVER_TEMP | 过温 | bit7
bitfield32 | Evt1 |  |  |  | OVER_FREQUENCY | 过频 | bit8
bitfield32 | Evt1 |  |  |  | UNDER_FREQUENCY | 欠频 | bit9
bitfield32 | Evt1 |  |  |  | AC_OVER_VOLT | AC过压 | bit10
bitfield32 | Evt1 |  |  |  | AC_UNDER_VOLT | AC欠压 | bit11
bitfield32 | Evt1 |  |  |  | BLOWN_STRING_FUSE (NOT implemented yet) | 保险已烧（未启用） | bit12
bitfield32 | Evt1 |  |  |  | UNDER_TEMP (NOT implemented yet) | 温度过低（未启用） | bit13
bitfield32 | Evt1 |  |  |  | MEMORY_LOSS | 内存错误 | bit14
bitfield32 | Evt1 |  |  |  | HW_TEST_FAILURE (NOT implemented yet) | 硬件检测失败（未启用） | bit15
0x0264（612） Event bitfield32 list
bitfield32 | Evt2 |  |  |  | Output ground fault | 输出接地故障 | bit0
bitfield32 | Evt2 |  |  |  | Grid phase lock failed | 电网锁相失败 | bit1
bitfield32 | Evt2 |  |  |  | Internal air over-temp | 内部环境温度过温 | bit2
bitfield32 | Evt2 |  |  |  | Grid-connected condition judgment timed out | 允许并网条件判断超时 | bit3
bitfield32 | Evt2 |  |  |  | Module renumber failure | 模块重号故障 | bit4
bitfield32 | Evt2 |  |  |  | CANB communication failure | CANB通信故障 | bit5
bitfield32 | Evt2 |  |  |  | Power frequency synchronization failure | 工频同步故障 | bit6
bitfield32 | Evt2 |  |  |  | Carrier synchronization failure | 载波同步故障 | bit7
bitfield32 | Evt2 |  |  |  | AC OVP | 交流过压 | bit8
bitfield32 | Evt2 |  |  |  | AC UVP | 交流欠压 | bit9
bitfield32 | Evt2 |  |  |  | AC OFP | 交流过频 | bit10
bitfield32 | Evt2 |  |  |  | AC UFP | 交流欠频 | bit11
bitfield32 | Evt2 |  |  |  | Grid voltage unbalance. | 电网电压不平衡 | bit12
bitfield32 | Evt2 |  |  |  | Grid phase reverse | 电网反序 | bit13
bitfield32 | Evt2 |  |  |  | Islanding | 逆变器孤岛 | bit14
bitfield32 | Evt2 |  |  |  | On/off grid switching error | 并离网切换异常 | bit15
Note on A78: The decade value of this register indcates the status
Note on A90: The decade value of this register indcates the status
Note on A109: The decade value of this register indcates the status

## Specified BMS Protocol
| Start | End | Size | Access | Type | Register Name | Units | Magnification | remarks
0x00A8 | 168 | 168 | 1 | W | uint16 | D.C._Voltage | V |  | BMS protocol for Vendor B | EP
0x00A9 | 169 | 169 | 1 | W | sunssf | D.C._Voltage_SF | SF |  | BMS protocol for Vendor B
0x00AA | 170 | 170 | 1 | W | uint16 | D.C._Current | A |  | BMS protocol for Vendor B
0x00AB | 171 | 171 | 1 | W | sunssf | D.C._Current_SF | SF |  | BMS protocol for Vendor B
0x00AC | 172 | 172 | 1 | W | uint16 | average_temp | C |  | BMS protocol for Vendor B
0x00AD | 173 | 173 | 1 | W | sunssf | average_temp_SF | SF |  | BMS protocol for Vendor B
0x00AE | 174 | 174 | 1 | W | uint16 | max_temp | C |  | BMS protocol for Vendor B
0x00AF | 175 | 175 | 1 | W | sunssf | max_temp_SF | SF |  | BMS protocol for Vendor B
0x00B0 | 176 | 176 | 1 | W | uint16 | min_Temp | C |  | BMS protocol for Vendor B
0x00B1 | 177 | 177 | 1 | W | sunssf | min_Temp_SF | SF |  | BMS protocol for Vendor B
0x00B2 | 178 | 178 | 1 | W | uint16 | max_cell_volt | V |  | BMS protocol for Vendor B
0x00B3 | 179 | 179 | 1 | W | sunssf | max_cell_volt_SF | SF |  | BMS protocol for Vendor B
0x00B4 | 180 | 180 | 1 | W | uint16 | min_cell_volt | V |  | BMS protocol for Vendor B
0x00B5 | 181 | 181 | 1 | W | sunssf | min_cell_volt_SF | SF |  | BMS protocol for Vendor B
0x00B6 | 182 | 182 | 1 | W | uint16 | average_cell_volt | V |  | BMS protocol for Vendor B
0x00B7 | 183 | 183 | 1 | W | sunssf | average_cell_volt_SF | SF |  | BMS protocol for Vendor B
0x00B8 | 184 | 184 | 1 | W | uint16 | soc |  |  | BMS protocol for Vendor B
0x00B9 | 185 | 185 | 1 | W | sunssf | soc_SF | SF |  | BMS protocol for Vendor B
0x00BA | 186 | 186 | 1 | W | uint16 | soh |  |  | BMS protocol for Vendor B
0x00BB | 187 | 187 | 1 | W | sunssf | soh_SF | SF |  | BMS protocol for Vendor B
0xF001 | 61441 | 61442 | 1 | W | uint16 | Battery total voltage | V | 10 | BMS protocol for Vendor A | 沃太/ALPHA-ESS
0xF002 | 61442 | 61443 | 1 | W | int16 | Battery total current | A | 10 | BMS protocol for Vendor A
0xF003 | 61443 | 61444 | 1 | W | uint16 | Battery SOC |  | 0.4% | BMS protocol for Vendor A
0xF004 | 61444 | 61445 | 1 | W | uint16 | Battery SOH |  | 0.4% | BMS protocol for Vendor A
0xF005 | 61445 | 61446 | 1 | W | uint16 | Battery status bits |  | \ | BMS protocol for Vendor A
0xF006 | 61446 | 61447 | 1 | W | uint16 | Battery error bits |  | \ | BMS protocol for Vendor A
0xF007 | 61447 | 61448 | 1 | W | uint16 | Battery error bits |  | \ | BMS protocol for Vendor A
0xF008 | 61448 | 61449 | 1 | W | uint16 | Battery error bits |  | \ | BMS protocol for Vendor A
0xF009 | 61449 | 61450 | 1 | W | int16 | Min temperature | C | 10 | BMS protocol for Vendor A
0xF00A | 61450 | 61451 | 1 | W | uint16 | Min temperature index |  | \ | BMS protocol for Vendor A
0xF00B | 61451 | 61452 | 1 | W | int16 | Max temperature | C | 10 | BMS protocol for Vendor A
0xF00C | 61452 | 61453 | 1 | W | uint16 | Max temperature index |  | \ | BMS protocol for Vendor A
0xF00D | 61453 | 61454 | 1 | W | int16 | Average temperature | C | 10 | BMS protocol for Vendor A
0xF00E | 61454 | 61455 | 1 | W | uint16 | Average voltage | V | 1000 | BMS protocol for Vendor A
0xF00F | 61455 | 61456 | 1 | W | uint16 | Min voltage | V | 1000 | BMS protocol for Vendor A
0xF010 | 61456 | 61457 | 1 | W | uint16 | Min voltage index |  | \ | BMS protocol for Vendor A
0xF011 | 61457 | 61458 | 1 | W | uint16 | Max voltage | V | 1000 | BMS protocol for Vendor A
0xF012 | 61458 | 61459 | 1 | W | uint16 | Max voltage index |  | \ | BMS protocol for Vendor A
0xF013 | 61459 | 61460 | 1 | W | uint16 | Max Allow charge current | A | 10 | BMS protocol for Vendor A
0xF014 | 61460 | 61461 | 1 | W | uint16 | Max Allow discharge current | A | 10 | BMS protocol for Vendor A
0xF015 | 61461 | 61462 | 1 | W | uint16 | BMS firmware version_LMU |  | 100 | BMS protocol for Vendor A
0xF016 | 61462 | 61463 | 1 | W | uint16 | BMS firmware version_BMU |  | 100 | BMS protocol for Vendor A
0xF017 | 61463 | 61464 | 1 | W | uint16 | BMS firmware version_Top BMU |  | 100 | BMS protocol for Vendor A
0xF018 | 61464 | 61465 | 1 | W | uint16 | BMS hardware version_LMU |  | 100 | BMS protocol for Vendor A
0xF019 | 61465 | 61466 | 1 | W | uint16 | BMS hardware version_BMU |  | 100 | BMS protocol for Vendor A
0xF01A | 61466 | 61467 | 1 | W | uint16 | BMS hardware version_Top BMU |  | 100 | BMS protocol for Vendor A
0xF01B | 61467 | 61468 | 1 | W | uint16 | 1~16 Cluster status |  | \ | BMS protocol for Vendor A
0xF01C | 61468 | 61469 | 1 | W | uint16 | 17~20 Cluster status |  | \ | BMS protocol for Vendor A
0x03E8 | 1000 | 1000 | 1 | R | uint16 | Basic Status基本状态 |  |  |  | 派能/PYLONTECH
0x03E9 | 1001 | 1001 | 1 | R | uint16 | Protection Status保护状态
0x03EA | 1002 | 1002 | 1 | R | uint16 | Alarm Status (see attached table)告警状态（详见附表）
0x03EB | 1003 | 1003 | 1 | R | uint16 | Total Voltage 总电压 | 0.1V | 10
0x03EC | 1004 | 1005 | 2 | R | uint32 | Current 电流 | 0.01A | 100
0x03EE | 1006 | 1006 | 1 | R | uint16 | Temperature 温度 | 0.1 ̊C | 10
0x03EF | 1007 | 1007 | 1 | R | uint16 | SOC | 0.01 | 100
0x03F0 | 1008 | 1008 | 1 | R | uint16 | Cycle Times 循环次数
0x03F1 | 1009 | 1009 | 1 | R | uint16 | Pile Max. Charge Voltage电池组最大充电电压值 | 0.1V | 10
0x03F2 | 1010 | 1011 | 2 | R | uint32 | Pile Max. Charge Current电池组最大充电电流值 | 0.01A | 100
0x03F4 | 1012 | 1012 | 1 | R | uint16 | Pile Min. Discharge Voltage电池组最小放电电压值 | 0.1V | 10
0x03F5 | 1013 | 1014 | 2 | R | uint32 | Pile Max. Discharge Current电池组最大放电电流值 | 0.01A | 100
0x03F7 | 1015 | 1015 | 1 | R | uint16 | Switch Value Indicate 开关量指示
0x03F8 | 1016 | 1016 | 1 | R | uint16 | Battery Cell Max. Voltage 电池最高电压 | 0.001V | 1000
0x03F9 | 1017 | 1017 | 1 | R | uint16 | Battery Cell Min. Voltage 电池最低电压 | 0.001V | 1000
0x03FA | 1018 | 1018 | 1 | R | uint16 | Battery Cell Max. Voltage Chanel 电池最高电压通道
0x03FB | 1019 | 1019 | 1 | R | uint16 | Battery Cell Min. Voltage Chanel电池最低电压通道
0x03FC | 1020 | 1020 | 1 | R | uint16 | Battery Cell Max. Temperature电池最高温度 | 0.1 ̊C | 10
0x03FD | 1021 | 1021 | 1 | R | uint16 | Battery Cell Min. Temperature电池最低温度 | 0.1 ̊C | 10
0x03FE | 1022 | 1022 | 1 | R | uint16 | Battery Cell Max. Temperature Chanel电池最高温度通道
0x03FF | 1023 | 1023 | 1 | R | uint16 | Battery Cell Min. Temperature Chanel电池最低温度通道
0x0400 | 1024 | 1024 | 1 | R | uint16 | Module Max. Voltage模块最高电压 | 0.01V | 100
0x0401 | 1025 | 1025 | 1 | R | uint16 | Module Min. Voltage模块最低电压 | 0.01V | 100
0x0402 | 1026 | 1026 | 1 | R | uint16 | Module Max. Voltage Chanel模块最高电压通道
0x0403 | 1027 | 1027 | 1 | R | uint16 | Module Min. Voltage Chanel模块最低电压通道
0x0404 | 1028 | 1028 | 1 | R | uint16 | Module Max. Temperature模块最高温度 | 0.1ºC | 10
0x0405 | 1029 | 1029 | 1 | R | uint16 | Module Min. Temperature模块最低温度 | 0.1ºC | 10
0x0406 | 1030 | 1030 | 1 | R | uint16 | Module Max. Temperature Chanel模块最高温度通道
0x0407 | 1031 | 1031 | 1 | R | uint16 | Module Min. Temperature Chanel模块最低温度通道
0x0408 | 1032 | 1032 | 1 | R | uint16 | SOH | 0.01 | 100
0x0409 | 1033 | 1034 | 2 | R | uint32 | Remain capacity 剩余容量 | Wh
0x040B | 1035 | 1036 | 2 | R | uint32 | Charge capacity蓄电池充电量 | Wh
0x040D | 1037 | 1038 | 2 | R | uint32 | Discharge capacity蓄电池放电量 | Wh
0x040F | 1039 | 1040 | 2 | R | uint32 | Daily accumulate charge capacity当日累积充电量 | Wh
0x0411 | 1041 | 1042 | 2 | R | uint32 | Daily accumulate discharge capacity当日累积放电量 | Wh
0x0413 | 1043 | 1044 | 2 | R | uint32 | History accumulate charge capacity历史累积充电量 | KWh
0x0415 | 1045 | 1046 | 2 | R | uint32 | History accumulate discharge capacity历史累积放电量 | KWh
0x0417 | 1047 | 1047 | 1 | R | uint16 | Request force charge mark强充标志位
0x0418 | 1048 | 1048 | 1 | R | uint16 | Request balance charge mark均衡充电标志位
0x0419 | 1049 | 1049 | 1 | R | uint16 | Pile number in parallel当前并联电池组数量
0x041A | 1050 | 1051 | 2 | R | uint32 | Error code 1故障代码1
0x041C | 1052 | 1053 | 2 | R | uint32 | Error code 2故障代码2
0x041E | 1054 | 1054 | 1 | R | uint16 | Number of battery modules in series connection in one pile电池组模块串联数
0x041F | 1055 | 1055 | 1 | R | uint16 | Number of cell in series in one pile电池组单体串联数
0x1080 | 4224 | 4224 | 1 | R | uint16 | 工作状态 |  |  | 0x1111（充满） 0x2222（放空） 0x5555（待机） 0xAAAA（停机） 0xBBBB（正常） | 协能/BMSER
0x1081 | 4225 | 4225 | 1 | R | uint16 | 系统可接受的最大充电电流 | A | 0.1A
0x1082 | 4226 | 4226 | 1 | R | uint16 | 系统可接受的最大放电电流 | A | 0.1A
0x1083 | 4227 | 4227 | 1 | R | uint16 | 系统总电压 | V | 0.1V
0x1084 | 4228 | 4228 | 1 | R | int16 | 系统总电流 | A | 0.1A | 充电为负，放电为正
0x1085 | 4229 | 4229 | 1 | R | uint16 | 系统 SOC | % |  | 0-100
0x1086 | 4230 | 4230 | 1 | R | uint16 | 系统 SOH | ‰ |  | 0-1000
0x1087 | 4231 | 4231 | 1 | R | uint16 | 第 1 支路并联状态 |  |  | 1：表示该支路在网（接触器处于闭合状态） 2：表示该支路断网（接触器处于断开状态）
0x1088 | 4232 | 4232 | 1 | R | uint16 | 第 2 支路并联状态
0x1089 | 4233 | 4233 | 1 | R | uint16 | 第 3 支路并联状态
0x108A | 4234 | 4234 | 1 | R | uint16 | 第 4 支路并联状态

## Fault code on LCD of PWS2-30M
serial | Fault Code | Fault | FaultinChinese
0 | 0 | AC overvoltage | 交流过压
1 | 1 | AC undervoltage | 交流欠压
2 | 2 | AC overfrequency | 交流过频
3 | 3 | AC underfrequency | 交流欠频
4 | 4 | Grid voltage asymmetric | 电网电压不平衡
5 | 5 | Phase reversed | 电网反序
6 | 6 | Inverter detects islanding | 逆变器孤岛
7 | 7 | Grid interconnection toggle failed | 并离网切换异常
8 | 8 | Ground fault | 输出接地故障
9 | 9 | PPL failed | 电网锁相失败
10 | A | Internal over temperature | 内部环境温度过温
11 | B | Grid checking timeout | 电网检测超时
12 | C | Module renumber failure | 模块重号故障
13 | D | CANB communication failure | CANB通信故障
14 | E | Power frequency synchronization failure | 工频同步故障
15 | F | Carrier synchronization failure | 载波同步故障
16 | 10 | Emergency power off | EPO
17 | 11 | Wrong parameter set | 监控参数设置故障
18 | 12 | DSP version fault | DSP版本故障
19 | 13 | CPLD version fault | CPLD版本故障
20 | 14 | Hardware version fault | 硬件版本故障
21 | 15 | CANA communication failed | CANA通信故障
22 | 16 | Aux power error | 15V电源故障
23 | 17 | Fan failed | 风扇故障,
24 | 18 | DC link overvoltage | 母线电压高
25 | 19 | DC link undervoltage | 母线电压低
26 | 1A | DC link voltage unbalanced | 母线电压不平衡
27 | 1B | Reserve | 预留
28 | 1C | AC relay short circuit | 交流继电器短路
29 | 1D | Abnormal output voltages | 输出电压异常
30 | 1E | Asymmetric current outputs | 输出电流不平衡
31 | 1F | Heatsink overheated | 散热器过温
32 | 20 | Overloaded timeout | 输出过载超时
33 | 21 | Grid countineously overvoltage | 电网连续过压
34 | 22 | AC soft start failed | 交流软启动失败
35 | 23 | Inverter start failed | 逆变启动失败
36 | 24 | AC relay open | 交流继电器开路
37 | 25 | Communication fault to secondary CPU | U2板通信故障
38 | 26 | Too much DC component | AC直流分量超额
39 | 27 | Master-slave sampling abnormal | 主从采样异常
40 | 28 | EEPROM reading error 1 | EE读取错误1
41 | 29 | EEPROM reading error 2 | EE读取错误2
42 | 2A | SPD error | 防雷器故障
43 | 2B | Over load | 逆变器过载
44 | 2C | Battery parameter setting error | 电池参数设置错误
45 | 2D | Slave lost alarm | 从机丢失告警
46 | 2E | Reserve | 预留
47 | 2F | Reserve | 预留
48 | 30 | Reserve | 预留
49 | 31 | Reserve | 预留
50 | 32 | Reserve | 预留
51 | 33 | Reserve | 预留
52 | 34 | Reserve | 预留
53 | 35 | Reserve | 预留
54 | 36 | Reserve | 预留
55 | 37 | Reserve | 预留
56 | 38 | DC input overvoltage | 直流输入过压
57 | 39 | DC input undervoltage | 直流输入欠压
58 | 3A | DC ground fault | 直流接地故障
59 | 3B | BMS alarm | BMS告警
60 | 3C | BMS connection timeout | BMS连接超时
61 | 3D | EMS connection timeout | EMS连接超时
62 | 3E | Reserve | 预留
63 | 3F | Reserve | 预留
64 | 40 | DC soft start failed | 直流软启动失败
65 | 41 | DC relay short circuit | 直流继电器短路
66 | 42 | DC relay open | 直流继电器开路
67 | 43 | Battery power overload timeout | 电池功率过载超时
68 | 44 | Bus soft start failed | 母线软启动失败
69 | 45 | DC fast detection overcurrent | 直流快检过流
70 | 46 | Reserve | 预留
71 | 47 | Reserve | 预留
72 | 48 | DC current overcurrent | 直流电流过流
144 | 90 | Parameter setting error | 参数下设错误
145 | 91 | Low off-grid energy | 离网能量低
146 | 92 | N line is not linked | N线未链接
147 | 93 | Standby bus height | 待机母线高
148 | 94 | Single-phase wiring error | 单相接线错误
149 | 95 | Frequency change rate excess | 频率变化率超额
150 | 96 | Grid phase angle mutation fault | 电网相角突变故障
151 | 97 | Off-Grid parameter conflict | 离网参数冲突