## Frame format
Frame format
PWS2-30K-NA supports RS485 or Ethernet， When implementing RS485, the baud rate is19200bps, verification: Modbus RTU Crc16 When deploying ethernet, the communication format conforms to ModBusTCP。
Reading format
Sending frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x03 | 0x00 | 0x00 | 0x00 | 0x0A | CRC
Response frame
Device address | Operation code | data quantily | data 1 | …… | data N | Verification
|  | (register quantity*2) |  |  |  | (L->H)
0x01 | 0x03 | 0x14(N) | XX | …… | XX | CRC
Writing format
Sending frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC
Response frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC

## PCS30kW-COMM_PROTOCOL
| Start | End | Size | Access | Register Name | Register Name in Chinese | Type | Unit | Comments | Magnification | Range(real value) | Default(real value) | Remark
0x0001 | 1 | 16 | 16 | R | model |  | String(32) |  | Manufacturer and model number
0x0011 | 17 | 24 | 8 | R | serial |  | String(16) |  | Serial Number
0x0020 | 32 | 32 | 1 | R | fault_occurred_0 |  | uint16x |  | Faults 15:0 occured |  |  |  | refer to "Status and fault list"
0x0021 | 33 | 33 | 1 | R | fault_occurred_1 |  | uint16x |  | Faults 31:16 occured |  |  |  | refer to "Status and fault list"
0x0022 | 34 | 34 | 1 | R | fault_occurred_2 |  | uint16x |  | Faults 47:32 occured |  |  |  | refer to "Status and fault list"
0x0023 | 35 | 35 | 1 | R | fault_occurred_3 |  | uint16x |  | Faults 63:48 occured |  |  |  | refer to "Status and fault list"
0x0024 | 36 | 36 | 1 | R | fault_occurred_4 |  | uint16x |  | Faults 79:64 occured |  |  |  | refer to "Status and fault list"
0x0025 | 37 | 37 | 1 | R | fault_occurred_5 |  | uint16x |  | Faults 95:80 occured |  |  |  | refer to "Status and fault list"
0x0026 | 38 | 38 | 1 | R | fault_occurred_6 |  | uint16x |  | Faults 111:96 occured |  |  |  | refer to "Status and fault list"
0x0027 | 39 | 39 | 1 | R | fault_occurred_7 |  | uint16x |  | Faults 127:112 occurred |  |  |  | refer to "Status and fault list"
0x0028 | 40 | 40 | 1 | R | fault_occurred_8 |  | uint16x |  | Faults 143:128 occurred |  |  |  | refer to "Status and fault list"
0x0029 | 41 | 41 | 1 | R | fault_occurred_9 |  | uint16x |  | Faults 159:144 occured |  |  |  | refer to "Status and fault list"
0x002A | 42 | 42 | 1 | R | fault_occurred_10 |  | uint16x |  | Faults 175:160 occured |  |  |  | refer to "Status and fault list"
0x002B | 43 | 43 | 1 | R | fault_occurred_11 |  | uint16x |  | Faults 191:176 occured |  |  |  | refer to "Status and fault list"
0x002C | 44 | 44 | 1 | R | fault_occurred_12 |  | uint16x |  | Faults 207:192 occured |  |  |  | refer to "Status and fault list"
0x002D | 45 | 45 | 1 | R | fault_occurred_13 |  | uint16x |  | Faults 223:208 occured |  |  |  | refer to "Status and fault list"
0x002E | 46 | 46 | 1 | R | fault_occurred_14 |  | uint16x |  | Faults 239:224 occured |  |  |  | refer to "Status and fault list"
0x002F | 47 | 47 | 1 | R | fault_occurred_15 |  | uint16x |  | Faults 255:240 occurred |  |  |  | refer to "Status and fault list"
0x0030 | 48 | 48 | 1 | R | fault_occurred_16 |  | uint16x |  | Faults 271:256 occured |  |  |  | refer to "Status and fault list"
0x0031 | 49 | 49 | 1 | R | fault_occurred_17 |  | uint16x |  | Faults 287:272 occured |  |  |  | refer to "Status and fault list"
0x0032 | 50 | 50 | 1 | R | fault_occurred_18 |  | uint16x |  | Faults 303:288 occured |  |  |  | refer to "Status and fault list"
0x0033 | 51 | 51 | 1 | R | fault_occurred_19 |  | uint16x |  | Faults 319:304 occured |  |  |  | refer to "Status and fault list"
0x0034 | 52 | 52 | 1 | R | fault_occurred_20 |  | uint16x |  | Faults 335:320 occured |  |  |  | refer to "Status and fault list"
0x0035 | 53 | 53 | 1 | R | fault_occurred_21 |  | uint16x |  | Faults 351:336 occured |  |  |  | refer to "Status and fault list"
0x0036 | 54 | 54 | 1 | R | fault_occurred_22 |  | uint16x |  | Faults 367:352 occured |  |  |  | refer to "Status and fault list"
0x0037 | 55 | 55 | 1 | R | fault_occurred_23 |  | uint16x |  | Faults 383:368 occurred |  |  |  | refer to "Status and fault list"
0x0038 | 56 | 56 | 1 | R | fault_occurred_24 |  | uint16x |  | Faults 399:384 occured |  |  |  | refer to "Status and fault list"
0x0039 | 57 | 57 | 1 | R | fault_occurred_25 |  | uint16x |  | Faults 415:400 occured |  |  |  | refer to "Status and fault list"
0x003A | 58 | 58 | 1 | R | fault_occurred_26 |  | uint16x |  | Faults 431:416 occured |  |  |  | refer to "Status and fault list"
0x003B | 59 | 59 | 1 | R | fault_occurred_27 |  | uint16x |  | Faults 447:432 occured |  |  |  | refer to "Status and fault list"
0x003C | 60 | 60 | 1 | R | fault_occurred_28 |  | uint16x |  | Faults 463:448 occured |  |  |  | refer to "Status and fault list"
0x003D | 61 | 61 | 1 | R | fault_occurred_29 |  | uint16x |  | Faults 479:464 occured |  |  |  | refer to "Status and fault list"
0x003E | 62 | 62 | 1 | R | fault_occurred_30 |  | uint16x |  | Faults 495:480 occured |  |  |  | refer to "Status and fault list"
0x003F | 63 | 63 | 1 | R | fault_occurred_31 |  | uint16x |  | Faults 512:496 occurred |  |  |  | refer to "Status and fault list"
0x0065 | 101 | 101 | 1 | R | InvOutVolt_A _Rms_Value | 模块端口AB线电压（*10） | int16 | V | AC A-B RMS voltage | ×10 |  |  | Indicates the A-B RMS voltage
0x0066 | 102 | 102 | 1 | R | InvOutVolt_B _Rms_Value | 模块端口BC线电压（*10） | int16 | V | AC B-C RMS voltage | ×10 |  |  | Indicates the B-C RMS voltage
0x0067 | 103 | 103 | 1 | R | InvOutVolt_C_Rms_value | 模块端口CA线电压（*10） | int16 | V | AC C-A RMS voltage | ×10 |  |  | Indicates the C-A RMS voltage
0x0068 | 104 | 104 | 1 | R | Analog_A_GridCurrent_Rms_Value | A相输出电流（*10） | int16 | A | AC phA RMS current | ×10 |  |  | Indicates the output current of Phase A
0x0069 | 105 | 105 | 1 | R | Analog_B_GridCurrent_Rms_Value | B相输出电流（*10） | int16 | A | AC phB RMS current | ×10 |  |  | Indicates the output current of Phase B
0x006A | 106 | 106 | 1 | R | Analog_C_GridCurrent_Rms_Value | C相输出电流（*10） | int16 | A | AC phC RMS current | ×10 |  |  | Indicates the output current of Phase C
0x006B | 107 | 107 | 1 | R | Analog_GridCurrent_Freq | 电网频率（*100） | int16 | Hz | AC frequency | ×100 |  |  | Indicates the frequency of the grid
0x006E | 110 | 110 | 1 | R | Analog_A_ActivePower_Rms_Value | A相有功功率（*100） | int16 | kW | AC phA Active Power | ×100 |  |  | Indicates the active power of Phase A
0x006F | 111 | 111 | 1 | R | Analog_B_ActivePower_Rms_Value | B相有功功率（*100） | int16 | kW | AC phB Active Power | ×100 |  |  | Indicates the active power of Phase B
0x0070 | 112 | 112 | 1 | R | Analog_C_ActivePower_Rms_Value | C相有功功率（*100） | int16 | kW | AC phC Active Power | ×100 |  |  | Indicates the active power of Phase C
0x0071 | 113 | 113 | 1 | R | Analog_A_ReactivePower_Rms_Value | A相无功功率（*100） | int16 | kVAR | AC phA Reactive Power | ×100 |  |  | Indicates the reactive power of Phase A
0x0072 | 114 | 114 | 1 | R | Analog_B_ReactivePower_Rms_Value | B相无功功率（*100） | int16 | kVAR | AC phB Reactive Power | ×100 |  |  | Indicates the reactive power of Phase B
0x0073 | 115 | 115 | 1 | R | Analog_C_ReactivePower_Rms_Value | C相无功功率（*100） | int16 | kVAR | AC phC Reactive Power | ×100 |  |  | Indicates the reactive power of Phase C
0x0074 | 116 | 116 | 1 | R | Analog_A_ApparentPower | A相视在功率（*100） | int16 | kVA | AC phA Apparent Power | ×100 |  |  | Indicates the apparent power of Phase A
0x0075 | 117 | 117 | 1 | R | Analog_B_ApparentPower | B相视在功率（*100） | int16 | kVA | AC phB Apparent Power | ×100 |  |  | Indicates the apparent power of Phase B
0x0076 | 118 | 118 | 1 | R | Analog_C_ApparentPower | C相视在功率（*100） | int16 | kVA | AC phC Apparent Power | ×100 |  |  | Indicates the apparent power of Phase C
0x0077 | 119 | 119 | 1 | R | Analog_A_PF_Rms_Value | A相功率因数（*100） | int16 | PF | AC phA Power Factor | ×100 |  |  | Indicates the power factor of Phase A
0x0078 | 120 | 120 | 1 | R | Analog_B_PF_Rms_Value | B相功率因数（*100） | int16 | PF | AC phB Power Factor | ×100 |  |  | Indicates the power factor of Phase B
0x0079 | 121 | 121 | 1 | R | Analog_C_PF_Rms_Value | C相功率因数（*100） | int16 | PF | AC phC Power Factor | ×100 |  |  | Indicates the power factor of Phase C
0x007A | 122 | 122 | 1 | R | Analog_ ActivePower_3Phase | 三相总有功功率（*100） | int16 | kW | AC Real Power | ×100 |  |  | Indicates the active power of the inverter
0x007B | 123 | 123 | 1 | R | Analog_ ReactivePower_3Phase | 三相总无功功率（*100） | int16 | kVAR | AC Reactive Power | ×100 |  |  | Indicates the reactive power of the inverter
0x007C | 124 | 124 | 1 | R | Analog_ ApparentPower_3Phase | 三相总视在功率（*100） | int16 | kVA | AC Apparent Power | ×100 |  |  | Indicates the apparent power of the inverter
0x007D | 125 | 125 | 1 | R | Analog_ PowerFactor_3Phase | 三相总PF值 | int16 |  | AC Power Factor | ×100 |  |  | Indicates the general power factor of the inverter
0x007E | 126 | 127 | 2 | RW | Analog_Dischg_Energy | 馈网电量（*10） | uint32 | kWh |  | ×10 |  |  | Not quite accurate, for reference only. Write 0 to reset the value
0x0080 | 128 | 129 | 2 | RW | Analog_Chg_Energy | 电网供电电量（*10） | uint32 | kWh |  | ×10 |  |  | Not quite accurate, for reference only. Write 0 to reset the value
0x0082 | 130 | 131 | 2 | R | Analog_Reactive_Energy | 无功电量（*10） | uint32 | kWh | Reactive energy | ×10 |  |  | useless in most cases
0x0084 | 132 | 132 | 1 | R | Temperature_Of_AC_ Heat_Sink | DCAC散热器温度（*1） | int16 | C | Temperature of AC heat sink | ×1
0x0085 | 133 | 133 | 1 | R | Positive_BUS_Voltage | 正母线电压*10 | int16 | V | BUS+ side voltage | ×10
0x0086 | 134 | 134 | 1 | R | Negtive_BUS_Voltage | 负母线电压*10 | int16 | V | BUS- side voltage | ×10
0x0087 | 135 | 135 | 1 | RW | Target_Active_Power | 有功功率期望 | int16 | kW | Target active power | ×10 | -30.0kW ~30.0kW | 0 | minus: charge, positive: discharge e.g.:10kw,write+100 to the inverter
0x0088 | 136 | 136 | 1 | RW | Target_Reactive_Power | 无功功率期望 | int16 | kVAR | Target reactive power | ×10 | -30.0kVAr~30.0kVAr | 0 | minus: inductive, positive: capacitive
0x0089 | 137 | 137 | 1 | RW | Target_Off-grid_Voltage | 离网电压期望 | int16 | V | Target off-grid voltage bias | ×100 | -0.05~+0.05(to rated voltage) | 0 | To regulate the off-grid AC volatge. Available only in off-gird mode
0x008A | 138 | 138 | 1 | RW | Target_Off-grid_Frequency | 离网频率期望 | int16 | Hz | Target off-grid frequency bias | ×100 | -2.0~2.0Hz | 0 | Available only in off-gird mode
0x008D | 141 | 141 | 1 | R | Analog_DC_Power | 直流功率（*100） | int16 | kW | DC power | ×100
0x008E | 142 | 142 | 1 | R | Analog_DC_Voltage | 直流电压（*10） | int16 | V | DC voltage | ×10
0x008F | 143 | 143 | 1 | R | Analog_DC_Current | 直流电流（*10） | int16 | A | DC current | ×10
0x0090 | 144 | 145 | 2 | RW | Analog_DC_Chg_Energy | 直流充电电量（*1） | uint32 | kWh | DC charged energy | ×1 |  |  | '0' value can be written to the register to reset their value
0x0092 | 146 | 147 | 2 | RW | Analog_ DC_Dischg_Energy | 直流放电电量（*1） | uint32 | kWh | DC discharged energy | ×1 |  |  | '0' value can be written to the register to reset their value
0x0094 | 148 | 148 | 1 | R | Temperature_Of_DCDC_Heat_Sink | DCDC散热器温度（*1） | int16 | C | Temperature of DC heat sink | ×1 |  |  | Indicates the
0x00A8 | 168 | 168 | 1 | R | D.C._Voltage | 直流电压 | uint16 | V | D.C. Voltage |  |  |  | BMS protocol for Vendor B Vendor B protocol is only for transferring the data from BMS via RS485 to EMS via Ethernet, no protection will be applied by inverter. Vendor A protocol provides protection and status display by inverter
0x00A9 | 169 | 169 | 1 | R | D.C._Voltage_SF | SF=Scale factor，下设倍率 | sunssf | SF | D.C. Voltage SF |  |  |  | BMS protocol for Vendor B
0x00AA | 170 | 170 | 1 | R | D.C._Current | 直流电流 | uint16 | A | D.C. Current |  |  |  | BMS protocol for Vendor B
0x00AB | 171 | 171 | 1 | R | D.C._Current_SF | SF=Scale factor，下设倍率 | sunssf | SF | D.C. Current SF |  |  |  | BMS protocol for Vendor B
0x00AC | 172 | 172 | 1 | R | average_temp | 平均温度 | uint16 | C | average temp |  |  |  | BMS protocol for Vendor B
0x00AD | 173 | 173 | 1 | R | average_temp_SF | SF=Scale factor，下设倍率 | sunssf | SF | average temp SF |  |  |  | BMS protocol for Vendor B
0x00AE | 174 | 174 | 1 | R | max_temp | 最大温度 | uint16 | C | max temp |  |  |  | BMS protocol for Vendor B
0x00AF | 175 | 175 | 1 | R | max_temp_SF | SF=Scale factor，下设倍率 | sunssf | SF | max temp SF |  |  |  | BMS protocol for Vendor B
0x00B0 | 176 | 176 | 1 | R | min_Temp | 最小温度 | uint16 | C | min Temp |  |  |  | BMS protocol for Vendor B
0x00B1 | 177 | 177 | 1 | R | min_Temp_SF | SF=Scale factor，下设倍率 | sunssf | SF | min Temp SF |  |  |  | BMS protocol for Vendor B
0x00B2 | 178 | 178 | 1 | R | max_cell_volt | 最大电池电压 | uint16 | V | max cell volt |  |  |  | BMS protocol for Vendor B
0x00B3 | 179 | 179 | 1 | R | max_cell_volt_SF | SF=Scale factor，下设倍率 | sunssf | SF | max cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B4 | 180 | 180 | 1 | R | min_cell_volt | 最小电池电压 | uint16 | V | min cell volt |  |  |  | BMS protocol for Vendor B
0x00B5 | 181 | 181 | 1 | R | min_cell_volt_SF | SF=Scale factor，下设倍率 | sunssf | SF | min cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B6 | 182 | 182 | 1 | R | average_cell_volt | 平均电池电压 | uint16 | V | average cell volt |  |  |  | BMS protocol for Vendor B
0x00B7 | 183 | 183 | 1 | R | average_cell_volt_SF | SF=Scale factor，下设倍率 | sunssf | SF | average cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B8 | 184 | 184 | 1 | R | soc | 电池已充电容量与电池额定容量的比值 | uint16 |  | SOC |  |  |  | BMS protocol for Vendor B
0x00B9 | 185 | 185 | 1 | R | soc_SF | SF=Scale factor，下设倍率 | sunssf | SF | soc SF |  |  |  | BMS protocol for Vendor B
0x00BA | 186 | 186 | 1 | R | soh | 电池可放出容量与新电池额定容量的比值 | uint16 |  | SOC |  |  |  | BMS protocol for Vendor B
0x00BB | 187 | 187 | 1 | R | soh_SF | SF=Scale factor，下设倍率 | sunssf | SF | soh SF |  |  |  | BMS protocol for Vendor B
0x012C | 300 | 303 | 4 | RW | IP_Address | IP地址 | uint64 |  | IP addreess |  |  |  | Takes effect after hard reset,set on the HMI,Default IP 192.168.0.10,node ID 1
0x0130 | 304 | 307 | 4 | RW | Netmask | 网络掩码 | uint64 |  | Netmask |  |  |  | Takes effect after hard reset
0x0134 | 308 | 311 | 4 | RW | Gateway | 网关IP地址 | uint64 |  | Gateway IP address |  |  |  | Takes effect after hard reset
0x0138 | 312 | 314 | 3 | RW | MAC | MAC地址,固定前两个字节00-24，后四个字节可修改 | uint48 |  | MAC address |  | fixed first 2 bytes as 00-24, the following 4 bytes is changeable, |  | Takes effect after hard reset
0x013C | 316 | 316 | 1 | RW | Modbus_Device_Address | Modbus设备地址 | uint16 |  | Modbus device address |  | 1~247 | 1 | Takes effect after hard reset
0x0140 | 320 | 320 | 1 | RW | baud_Rate | 接口波特率，单位为位/秒 | enum16 |  | Interface baud rate in bits per second |  | 0: 19200, 1: 9600 | 0 | Takes effect after hard reset
0x0145 | 325 | 325 | 1 | RW | Interface Type | 接口类型 | enum16 |  | EMS Interface type |  | 0: RS-485, 1: Ethernet | 0 | if implement RS-485 as EMS interface. BMS access is invalid TCP and RS485 can be used，TCP is recommended
0x0146 | 326 | 326 | 1 | RW | Protocol_Selection | 串行协议选择 0-modbus 1-sunspec;默认1 | enum16 |  | Serial protocol selection |  | 0: modbus 1: sunspec | 1 | should not be changed after 2017 old protocol is not used in the new products some redundant registers are both in the sunspec section and other sections.
0x0147 | 327 | 327 | 1 | RW | EMS timeout setting | EMS超时时间 | uint16 | s | 0=disabled | ×1 | 0~32767 | 0 | Prevent unexpected results of communication failures.when EMS timeout enabled, watchdog will work and even reading will feed the watchdog
0x0148 | 328 | 328 | 1 | RW | EPO enable/disable | EPO使能 | enum16 |  | EPO enableing |  | 0: disabled, 1: enabled | 0 | Enable ONLY when remote Emergency Stop Button is needed
0x0149 | 329 | 329 | 1 | RW | BMS timeout setting | BMS超时时间 | uint16 | s | 0=disabled | ×1 | 0~32767 | 0 | Enable ONLY when remote BMS-inverter connection is needed
0x014A | 330 | 330 | 1 | RW | Adapted BMS protocol | BMS协议选择 | uint16 |  |  |  | 0=Vender B 1=Vendor A 2=Vendor P |  | Added in V2052
0x014B | 331 | 331 | 1 | RW | Boot from grid-tied or off-grid | 启动时并网状态 | uint16 |  | Select which mode the PCS will start when it's powerer |  | 0=grid-tied 1=off-grid | 0 | Added in V2052
SUNSPEC/MESA SECTION- START
0x01F4 | 500 | 501 | 2 | R | SunSpec_ID | 知名价值。唯一标识这是一个SunSpec Modbus地图 | uint32x |  | Well-known value. Uniquely identifies this as a SunSpec Modbus Map
0x01F6 | 502 | 502 | 1 | R | SunSpec_DID_0001 | 唯一标识这是一个SunSpec公共模型块 | uint16 |  | Uniquely identifies this as a SunSpec Common Model Block
0x01F7 | 503 | 503 | 1 | R | SunSpec_Length_0001 | 16位寄存器中的块长度 | uint16 |  | Length of block in 16-bit registers
0x01F8 | 504 | 519 | 16 | R | Manufacturer |  | string |  | Manufacturer
0x0208 | 520 | 535 | 16 | R | Model | 制造商特定值（32个字符） | string |  | Manufacturer specific value (32 chars)
0x0218 | 536 | 543 | 8 | R | Options | 制造商特定值（16个字符） | string |  | Manufacturer specific value (16 chars) |  | 波特率+数据位+停止位+校验位
0x0220 | 544 | 551 | 8 | R | Version | 制造商特定值（16 chars） | string |  | Manufacturer specific value (16 chars)
0x0228 | 552 | 567 | 16 | R | Serial Number | 制造商特定值（32个字符） | string |  | Manufacturer specific value (32 chars)
0x0238 | 568 | 568 | 1 | RW | Device Address | Modbus设备地址 | uint16 |  | Modbus device address
0x0239 | 569 | 569 | 1 | R | pad | 强制均匀对齐 | pad |  | Force even alignment
0x023A | 570 | 570 | 1 | R | SunSpec_DID_0103 | 103 - 三相逆变器 | uint16 |  | 103 - 3-phase inverter
0x023B | 571 | 571 | 1 | R | SunSpec_Length_0103 | 模型块在寄存器中的长度 | uint16 |  | Length of model block in registers
0x023C | 572 | 572 | 1 | R | Amps | 交流电流 | uint16 | A | AC Current
0x023D | 573 | 573 | 1 | R | Amps PhaseA | A相电流 | uint16 | A | Phase A Current
0x023E | 574 | 574 | 1 | R | Amps PhaseB | B相电流 | uint16 | A | Phase B Current
0x023F | 575 | 575 | 1 | R | Amps PhaseC | C相电流 | uint16 | A | Phase C Current
0x0240 | 576 | 576 | 1 | R | A_SF | 交流电流​​比例系数 | sunssf | SF | AC Current Scale factor
0x0241 | 577 | 577 | 1 | R | PPVphAB | AB线电压 | uint16 | V | Phase Voltage AB
0x0242 | 578 | 578 | 1 | R | PPVphBC | BC线电压 | uint16 | V | Phase Voltage BC
0x0243 | 579 | 579 | 1 | R | PPVphCA | CA线电压 | uint16 | V | Phase Voltage CA
0x0244 | 580 | 580 | 1 | R | PhVphA | A相电压 | uint16 | V | Phase Voltage AN
0x0245 | 581 | 581 | 1 | R | PhVphB | B相电压 | uint16 | V | Phase Voltage BN
0x0246 | 582 | 582 | 1 | R | PhVphC | C相电压 | uint16 | V | Phase Voltage CN
0x0247 | 583 | 583 | 1 | R | V_SF | 交流电压比例系数 | sunssf | SF | AC Voltage Scale factor
0x0248 | 584 | 584 | 1 | R | Watts | 交流功率 | int16 | W | AC Power
0x0249 | 585 | 585 | 1 | R | W_SF | 交流功率比例系数 | sunssf | SF | AC Power Scale factor
0x024A | 586 | 586 | 1 | R | Hz | 线路频率 | uint16 | Hz | Line Frequency
0x024B | 587 | 587 | 1 | R | Hz_SF | 比例系数 | sunssf | SF | Scale factor
0x024C | 588 | 588 | 1 | R | VA | 交流视在功率 | int16 | VA | AC Apparent Power
0x024D | 589 | 589 | 1 | R | VA_SF | 比例系数 | sunssf | SF | Scale factor
0x024E | 590 | 590 | 1 | R | Var | 交流无功功率 | int16 | var | AC Reactive Power
0x024F | 591 | 591 | 1 | R | VAr_SF | 比例系数 | sunssf | SF | Scale factor
0x0250 | 592 | 592 | 1 | R | PF | 交流功率因数 | int16 | Pct | AC Power Factor
0x0251 | 593 | 593 | 1 | R | PF_SF | 比例系数 | sunssf | SF | Scale factor
0x0252 | 594 | 595 | 2 | R | WattHours | 交流能量 | acc32 | Wh | AC Energy
0x0254 | 596 | 596 | 1 | R | WH_SF | 比例系数 | sunssf | SF | Scale factor
0x0255 | 597 | 597 | 1 | R | DC Amps | 直流电流 | uint16 | A | DC Current
0x0256 | 598 | 598 | 1 | R | DCA_SF | 比例系数 | sunssf | SF | Scale factor
0x0257 | 599 | 599 | 1 | R | DC Voltage | 直流电压 | uint16 | V | DC Voltage
0x0258 | 600 | 600 | 1 | R | DCV_SF | 比例系数 | sunssf | SF | Scale factor
0x0259 | 601 | 601 | 1 | R | DC Watts | 直流功率（*100） | int16 | W | DC Power | ×100
0x025A | 602 | 602 | 1 | R | DCW_SF | 比例系数 | sunssf | SF | Scale factor
0x025B | 603 | 603 | 1 | R | Cabinet Temperature | 机柜温度 | int16 | C | Cabinet Temperature
0x025C | 604 | 604 | 1 | R | Heat Sink Temperature | 散热器温度 | int16 | C | Heat Sink Temperature |  |  |  | DCAC circuit heat sink
0x025D | 605 | 605 | 1 | R | Transformer Temperature | 变压器温度 | int16 | C | Transformer Temperature |  |  |  | No transformer
0x025E | 606 | 606 | 1 | R | Other Temperature | 其他温度 | int16 | C | Other Temperature |  |  |  | DCDC circuit heat sink
0x025F | 607 | 607 | 1 | R | Tmp_SF | 温度比例系数 | sunssf |  | Scale factor
0x0260 | 608 | 608 | 1 | R | Operating State | 枚举值。工作状态 | enum16 |  | Enumerated value. Operating state |  |  |  | report the current operating status of the inverter
0x0261 | 609 | 609 | 1 | R | Vendor Operating State | 操作状态代码 | enum16 |  | Vendor specific operating state code
0x0262 | 610 | 611 | 2 | R | Event1 | 位阈事件 | bitfield32 |  | Bitmask value. Event fields
0x0264 | 612 | 613 | 2 | R | Event Bitfield 2 | Faults 95:64 occured | bitfield32 |  | Vendor defined events |  |  |  | Faults 95:64 occured
0x0266 | 614 | 615 | 2 | R | Vendor Event Bitfield 1 | Faults 127:96 occured | bitfield32 |  | Vendor defined events |  |  |  | Faults 127:96 occured
0x0268 | 616 | 617 | 2 | R | Vendor Event Bitfield 2 | Faults 159:128 occurred | bitfield32 |  | Vendor defined events |  |  |  | Faults 159:128 occurred
0x026A | 618 | 619 | 2 | R | Vendor Event Bitfield 3 | Faults 191:160 occured | bitfield32 |  | Vendor defined events |  |  |  | Faults 191:160 occured
0x026C | 620 | 621 | 2 | R | Vendor Event Bitfield 4 | Faults 223:192 occured | bitfield32 |  | Vendor defined events |  |  |  | Faults 223:192 occured
0x026E | 622 | 622 | 1 | R | SunSpec_DID_FFFF | SunSpec终止块 | uint16 |  | SunSpec End Block
0x026F | 623 | 623 | 1 | R | SunSpec_Length_FFFF | 结束块的长度 | uint16 |  | Length of End Block
SUNSPEC/MESA SECTION- END
0x028A | 650 | 650 | 1 | RW | SETDATA_ModOnCmd | 开机 | enum16 |  |  |  | 1: true, other: illegal |  | To Start operation, only 1 will be accepted. Reading back value makes no sense
0x028B | 651 | 651 | 1 | RW | SETDATA_ModOffCmd | 关机 | enum16 |  |  |  | 1: true, other: illegal |  | To Stop operation, only 1 will be accepted. Reading back value makes no sense
0x028C | 652 | 652 | 1 | RW | SETDATA_ClearFailureCmd | 清除故障 | enum16 |  | Clearing fault |  | 1: true, other: illegal |  | clear failure flag,when fault occurs, the system will stop and indicates fault. starting is invalid until the fault source is actually removed and this register is written 1. Reading back value makes no sense
0x028D | 653 | 653 | 1 | RW | SETDATA_OnGridCmd | 并网 | enum16 |  | grid mode |  | 1: true, other: illegal |  | set the module to on grid mode. Reading back value makes no sense
0x028E | 654 | 654 | 1 | RW | SETDATA_OffGridCmd | 离网 | enum16 |  | off grid mode |  | 1: true, other: illegal |  | set the module to off grid mode. Reading back value makes no sense
0x028F | 655 | 655 | 1 | RW | SETDATA_StandbyCmd | 待机 | enum16 |  | standby(idle) mode |  | 1: true, other: illegal |  | set the module to standby mode,setpoint 0:IGBT switching ,setpoint 1:no IGBT switching,low consumption.let the inverter to halt the IGBT switching, to save the power consumption, but all relays are still closed. Reading back value makes no sense
0x02EC | 748 | 748 | 1 | R | Output voltage | 输出电压等级 | enum16 |  | Output voltage level |  | 0: 380V, 1: 400V, 2: 480V | 0 | Internal function, shall not be changed as will
0x02ED | 749 | 749 | 1 | R | Output frequency | 输出频率等级：50Hz/60Hz | enum16 |  | Output frequency level: 50 Hz / 60 Hz |  | 0: 50Hz, 1 60Hz, | 0 | Internal function, shall not be changed as will
0x02EE | 750 | 750 | 1 | R | Grid type | 输出电压体制：三相四线制/三相三线制 | enum16 |  | Output voltage system: Three-phase four-wire / three-phase three-wire system |  | 0: 3P4W, 1: 3P3W or 3P3W+N | 2 | Internal function, shall not be changed as will
0x02F1 | 753 | 753 | 1 | R | output power Rating | 模块功率等级:10kW/20kW/30kW | enum16 |  | Module power: 10 kW / 20 kW / 30 kW |  | 0: 10kW, 1: 20kW, 2: 30kW, 3: 29kW |  | Internal function, shall not be changed as will
0x02F2 | 754 | 754 | 1 | R | DC voltage level 750/830 | 未启用 | enum16 |  | Not Implemented yet |  | 0-750；1-830； | 0 | Internal function, shall not be changed as will
0x0300 | 768 | 768 | 1 | RW | ac_ov_trip_level_1 | 电网过压I段保护幅值(IEEE1547) | int16 | %Vrated | ratio | ×100 | 1.05~1.2 | 1.1
0x0301 | 769 | 769 | 1 | RW | ac_ov_trip_time_1 | 电网过压I段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~13s | 1
0x0302 | 770 | 770 | 1 | RW | ac_ov_trip_level_2 | 电网过压Ⅱ段保护幅值(IEEE1547) | int16 | %Vrated | ratio | ×100 | 1.05~1.2 | 1.1
0x0303 | 771 | 771 | 1 | RW | ac_ov_trip_time_2 | 电网过压Ⅱ段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~0.16s | 0.16
0x0304 | 772 | 772 | 1 | RW | ac_uv_trip_level_1 | 电网欠压I段保护幅值(IEEE1547) | int16 | %Vrated | ratio | ×100 | 0. 45~0.95 | 0.88
0x0305 | 773 | 773 | 1 | RW | ac_uv_trip_time_1 | 电网欠压I段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~21s | 2
0x0306 | 774 | 774 | 1 | RW | ac_uv_trip_level_2 | 电网欠压Ⅱ段保护幅值(IEEE1547) | int16 | %Vrated | ratio | ×100 | 0. 45~0.95 | 0.6
0x0307 | 775 | 775 | 1 | RW | ac_uv_trip_time_2 | 电网欠压Ⅱ段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~11s | 1
0x0308 | 776 | 776 | 1 | RW | ac_uv_trip_level_3 | 电网欠压Ⅲ段保护幅值(IEEE1547) | int16 | %Vrated | ratio | ×100 | 0.45~0.95 | 0.45
0x0309 | 777 | 777 | 1 | RW | ac_uv_trip_time_3 | 电网欠压Ⅲ段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~0.16s | 0.16
0x030A | 778 | 778 | 1 | RW | ac_of_trip_level_1 | 电网过频I段保护幅值(IEEE1547) | int16 | Hz |  | ×100 | 0~4.5Hz | 0.5
0x030B | 779 | 779 | 1 | RW | ac_of_trip_time_1 | 电网过频I段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0-300s | 2
0x030C | 780 | 780 | 1 | RW | ac_of_trip_level_2 | 电网过频Ⅱ段保护幅值(IEEE1547) | int16 | Hz |  | ×100 | 0~4.5Hz | 2
0x030D | 781 | 781 | 1 | RW | ac_of_trip_time_2 | 电网过频Ⅱ段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~10s | 0.16
0x030E | 782 | 782 | 1 | RW | ac_uf_trip_level_1 | 电网欠频I段保护幅值(IEEE1547) | int16 | Hz |  | ×100 | -4.5~0Hz | -1
0x030F | 783 | 783 | 1 | RW | ac_uf_trip_time_1 | 电网欠频I段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0-300s | 2
0x0310 | 784 | 784 | 1 | RW | ac_uf_trip_level_2 | 电网欠频Ⅱ段保护幅值(IEEE1547) | int16 | Hz |  | ×100 | -4.5~0Hz | -2
0x0311 | 785 | 785 | 1 | RW | ac_uf_trip_time_2 | 电网欠频Ⅱ段保护时间 (IEEE1547) | int16 | s |  | ×100 | 0~10s | 0.16
0x0312 | 786 | 786 | 1 | RW | reconnect_time | 电网恢复延时(IEEE1547) | int16 | s |  | ×1 | 35~300s | 50 | default value
0x0316 | 790 | 790 | 1 | RW | Anti-islanding function | 孤岛检测 | enum16 |  | Island detection |  | 0: disabled, 1: enabled |  | Anti-islanding is a CPUC RULE 21/HECO RULE14H/IEEE1547-requested function to make sure the inverter disconnect from the grid in case of blackout. This is to prevent the formation of an unintended island. The inverter design shall comply with the requirements of IEEE Std 1547 and UL 1741 standards (or latest versions) and be certified to have anti-islanding protection such that the synchronous inverter will automatically disconnect upon a utility system interruption
0x0317 | 791 | 791 | 1 | RW | FVRT function | 频率/电压穿越功能使能 | enum16 |  |  |  | 0: disabled, 1: enabled | 0 | Frequency and Voltage Ride-Through. The ability to withstand voltage or frequency excursions outside defined limits without tripping or malfunctioning
0x0318 | 792 | 792 | 1 | RW | Reactive power control mode | 无功功率调整模式 | enum16 |  | Reactive power regulation mode |  | 0: Constant reactive power 1: Volt-VAr enabled 2: Constant PF 3: Watt-PF enabled (VDE) | 0 | Grid-tied mode only, voltage and frequency setpoint the only setpoints
0x0319 | 793 | 793 | 1 | RW | Power rising mode | 功率变化模式:0-阶跃， 1-斜率 | enum16 |  | Power change mode |  | 0: step, 1: ramp(soft-start) | 0 | to define how the power changes
0x031A | 794 | 794 | 1 | RW | Active power control mode | 有功功率调节模式： 0-恒定有功功率，禁用1/2/3 1-电压自动调节，在电压正常范围内按0执行，电压超过一定范围自动按电压偏差量调节有功功率 2-频率自动调节(Freq/Volt)在频率正常范围内按0执行，频率超过一定范围自动按偏差量调节有功功率 3-电压频率自动调节(Volt/Watt & Freq/Watt) 电压频率均正常时执行0，异常时执行Freq/Watt 优先于Volt/Watt | enum16 |  | Active power regulation mode |  | 0: Constant Active power 1: Volt-Watt enabled 2: Freq-Watt enabled 3: Volt-Watt + Freq-Watt enabled | 0 | Grid-tied mode only, Volt/Watt control & Freq/Watt control means active power will be regulated by grid voltage/frequency following a curve/ramp rate given by HECO or CPUC or other local utility authority codes
0x031B | 795 | 795 | 1 | RW | Grid voltage asymmetric detection | 电网电压不平衡检测使能 | enum16 |  | Power grid voltage imbalance detection enable |  | 0: disabled, 1: enabled | 1 | Grid-tied mode only, voltage and frequency setpoint the only setpoints
0x031C | 796 | 796 | 1 | RW | continuous overvoltage detection | 连续过压检测使能 | enum16 |  | Continuous overvoltage detection enable |  | 0: disabled, 1: enabled | 1 | Grid-tied mode only
0x031D | 797 | 797 | 1 | RW | Grid-existence detection on power-up | 并网开机电网检测使能 | enum16 |  | Grid-connected power grid detection enable |  | 0: disabled, 1: enabled | 1 | Grid-tied mode only,detect whether the grid is on-service at powered-up.
0x031E | 798 | 798 | 1 | RW | Neutral floating detection | 缺N检测使能 | enum16 |  | 缺N检测使能 |  | 0: disabled, 1: enabled | 1 | Grid-tied mode only
0x031F | 799 | 799 | 1 | RW | Off-grid black-start mode | 离网黑启动方式 | enum16 |  | 离网黑启动方式 |  | 0: disabled, 1: enabled | 0 | if disabled, the inverter will start the AC voltage, then close the relay. In some off-grid cases, such as there are inductive loads or transformer, the inrush exciting current will trip the inverter. Enabling this register, the inverter will close the relay first try to limit the current and start the voltage slowly
0x0320 | 800 | 800 | 1 | RW | Grid code selection | 并网标准选择 | enum16 |  | Select region |  | 0: HECO 14H /CPUC 21 (UL 1741SA) 1:VDE4105 2:AS4777 | 0 | Grid-tied mode only
0x0328 | 808 | 808 | 1 | RW | Float charge voltage | 浮充电压 | int16 | V | 锂电池二者要设为相同 | ×10 | 200.0~800.0V | 550V | when implementing Lithium-ion batteries, these two registers MUST be set to the same
0x0329 | 809 | 809 | 1 | RW | Topping charge volage | 恒压充电压 | int16 | V |  | ×10 | 200.0~800.0V | 550V
0x032A | 810 | 810 | 1 | RW | Current from topping charging to float charging | 恒压充转浮充电流 | int16 | A | 锂电池设为0 | ×10 | 0.0~90.0A | 10A | when implementing Lithium-ion batteries,this register MUST be set to 0
0x032B | 811 | 811 | 1 | RW | Max charging current | 最大充电电流 | int16 | A |  | ×10 | 0.0~90.0A | 90A | limit the max DC currents, keep default if you don't need to
0x032C | 812 | 812 | 1 | RW | Max discharging current | 最大放电电流 | int16 | A |  | ×10 | 0.0~90.0A | 90A | limit the min DC currents, keep default if you don't need to
0x032D | 813 | 813 | 1 | RW | Lower voltage limit of battery protection | 电池电压下限保护阈值 | int16 | V | Battery voltage lower protection threshold | ×10 | 200.0~800.0V | 200V
0x032E | 814 | 814 | 1 | RW | Upper voltage limit of battery protection | 电池电压上限保护阈值 | int16 | V |  | ×10 | 200.0~800.0V | 600V | this register can't be set lower than 0x0328 and 0x0329
0x033C | 828 | 828 | 1 | RW | FVRT: Over/High voltage stage I ride through voltage ratio | 过(高)压穿越I段幅值(比率) | int16 | %Vrated |  | 100 | 1.10~1.20 | 1.1 | ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x033D | 829 | 829 | 1 | RW | FVRT: Over/High voltage stage II ride through voltage ratio | 过(高)压穿越II段幅值(比率) | int16 | %Vrated |  | 100 | 1.10~1.20 | 1.2 | ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x033E | 830 | 830 | 1 | RW | FVRT: Under/Low voltage stage I ride through voltage ratio | 欠(低)压穿越I段幅值(比率) | int16 | %Vrated |  | 100 | 0.50~0.88 | 0.8 | ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x033F | 831 | 831 | 1 | RW | FVRT: Under/Low voltage stage II ride through voltage ratio | 欠(低)压穿越II段幅值(比率) | int16 | %Vrated |  | 100 | 0.50~0.88 | 0.6 | ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0340 | 832 | 832 | 1 | RW | FVRT: Under/Low voltage stage III ride through voltage ratio | 欠(低)压穿越III段幅值(比率) | int16 | %Vrated |  | 100 | 0.40-0.50 | 0.5 | ratio * rated voltage, follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0341 | 833 | 833 | 1 | RW | FVRT: Over frequency stage I ride through frequency | 过频穿越I段频率 | int16 | Hz | Bias from rated frequency | 100 | 1~6Hz | 3Hz | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0342 | 834 | 834 | 1 | RW | FVRT: Over frequency stage II ride through frequency | 过频穿越II段频率 | int16 | Hz | Bias from rated frequency | 100 | 2~6Hz | 5Hz | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0343 | 835 | 835 | 1 | RW | FVRT: Under frequency stage I ride through frequency | 欠频穿越I段频率 | int16 | Hz | Bias from rated frequency | 100 | -10~-0.1Hz | -3Hz | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0344 | 836 | 836 | 1 | RW | FVRT: Under frequency stage II ride through frequency | 欠频穿越II段频率 | int16 | Hz | Bias from rated frequency | 100 | -10~-0.1Hz | -10Hz | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0345 | 837 | 837 | 1 | RW | FVRT: Over/High voltage stage I ride through trip time | 过(高)压穿越I段时间 | int16 | s |  | 100 | 0.08-12.00s | 12s | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0346 | 838 | 838 | 1 | RW | FVRT: Over/High voltage stage II ride through trip time | 过(高)压穿越II段时间 | int16 | s |  | 100 | 0.08-0.16s |  | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0347 | 839 | 839 | 1 | RW | FVRT: Under/Low voltage stage I ride through trip time | 欠(低)压穿越I段时间 | int16 | s |  | 100 | 20.00-50.00s | 20s | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0348 | 840 | 840 | 1 | RW | FVRT: Under/Low voltage stage II ride through trip time | 欠(低)压穿越II段时间 | int16 | s |  | 100 | 10.00-50.00s | 10s | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x0349 | 841 | 841 | 1 | RW | FVRT: Under/Low voltage stage III ride through trip time | 欠(低)压穿越III段时间 | int16 | s |  | 100 | 0.08-21.00s | 0.5s | follow the FVRT table given by HECO or CPUC or other local utility authority codes
0x034A | 842 | 842 | 1 | RW | FVRT: Over frequency stage I ride through trip time | 过频穿越I段穿越时间 | int16 | s |  | 10 | 20-1000.00s | 20.s
0x034B | 843 | 843 | 1 | RW | FVRT: Over frequency stage II ride through trip time | 过频穿越II段穿越时间 | int16 | s |  | 100 | 0-1000.00s | 0.1s
0x034C | 844 | 844 | 1 | RW | FVRT: Under frequency stage I ride through trip time | 欠频穿越I段穿越时间 | int16 | s |  | 10 | 20-1000.00s | 20.s
0x034D | 845 | 845 | 1 | RW | FVRT: Under frequency stage II ride through trip time | 欠频穿越II段穿越时间 | int16 | s |  | 10 | 0-1000.00s | 0.1s
0x0350 | 848 | 848 | 1 | RW | Volt-VAr: reference voltage Vref | 电压调无功:调节参考电压Vref(HECO) | int16 | %Vrated | ratio | 1000 | 0.950~1.050 | 1 | refer to HECO RULE 14, keep default value if no aware of it
0x0351 | 849 | 849 | 1 | RW | Volt-VAr: V1, Voltage setpoint @ Q1 | 电压调无功: 调节点V1 | int16 | %Vrated | ratio | 1000 | 0.820~1.030 | 0.92 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0352 | 850 | 850 | 1 | RW | Volt-VAr: V2, Voltage setpoint @ Q2 | 电压调无功: 调节点V2 | int16 | %Vrated | ratio | 1000 | 0.900~1.050 | 0.98 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0353 | 851 | 851 | 1 | RW | Volt-VAr: V3, Voltage setpoint @ Q3 | 电压调无功: 调节点V3 | int16 | %Vrated | ratio | 1000 | 0.950~1.150 | 1.02 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0354 | 852 | 852 | 1 | RW | Volt-VAr: V4, Voltage setpoint @ Q4 | 电压调无功: 调节点V4 | int16 | %Vrated | ratio | 1000 | 0.970~1.180 | 1.06 | ratio * rated voltage, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0355 | 853 | 853 | 1 | RW | Volt-VAr: Q1, Max capacitive reactive regulation | 电压调无功:最大容性无功调节量Q1 | int16 | %Srated | ratio | 100 | 0~0.6 | 0.3 | ratio * rated power, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0356 | 854 | 854 | 1 | RW | Volt-VAr: Q2, Initial capacitive reactive regulation | 电压调无功:初始容性无功调节量Q2 | int16 | %Srated | ratio | 100 | 0~0.6 | 0 | ratio * rated power, Available only when reactive power regulation mode is set to Volt/Var(53626).
0x0357 | 855 | 855 | 1 | RW | Volt-VAr: Q3, Initial inductive reactive regulation | 电压调无功:初始感性无功调节量Q3 | int16 | %Srated | ratio | 100 | 0~0.6 | 0 | refer to HECO RULE 14, keep default value if no aware of it
0x0358 | 856 | 856 | 1 | RW | Volt-VAr: Q4, Max inductive reactive regulation | 电压调无功:最大感性无功调节量Q4 | int16 | %Srated | ratio | 100 | 0~0.6 | 0.3 | refer to HECO RULE 14, keep default value if no aware of it
0x0359 | 857 | 857 | 1 | RW | Volt-VAr: response time | 电压调无功:调节反应时间 | int16 | s |  | 100 | 1~90s | 10s | refer to HECO RULE 14, keep default value if no aware of it
0x035E | 862 | 862 | 1 | RW | Volt-Watt: initial voltage Vstart | 过压降有功起始调节点Vstart | int16 | %Vrated | ratio | 1000 | 1.010~1.200 | 1.06 | ratio * rated voltage, Available only when active power regulation mode(53636) is set to Volt/Watt and operating in discharge mode, follow the FVRT table given by HECO or CPUC or other local utility authority codes.
0x035F | 863 | 863 | 1 | RW | Volt-Watt: end voltage Vstop | 过压降有功终止调节点Vstop | int16 | %Vrated | ratio | 1000 | 1.020~1.200 | 1.1 | refer to HECO RULE 14, keep default value if no aware of it
0x0360 | 864 | 864 | 1 | RW | Volt-Watt: initial power Pstart | 过压降有功起始功率Pstart | int16 | %Ppresent | ratio | 100 | 0.00~1.00 | 1 | refer to HECO RULE 14, keep default value if no aware of it
0x0361 | 865 | 865 | 1 | RW | Volt-Watt: end power Pstop | 过压降有功终止功率Pstop | int16 | %Ppresent | ratio | 100 | 0.00~1.00 | 0 | refer to HECO RULE 14, keep default value if no aware of it
0x0362 | 866 | 866 | 1 | RW | Volt-Watt: return to service delay | 过压降有功恢复延时 | int16 | s |  | 100 | 3~90s | 60s | To set the output power recovery time delay after the utility voltage returns to normal
0x0363 | 867 | 867 | 1 | RW | Volt-Watt: response time | 过压降有功反应时间 | int16 | s | CPUC rule 21 only | 100 | 0.5-60s | 10s | refer to HECO RULE 14, keep default value if no aware of it
0x0364 | 868 | 868 | 1 | RW | Freq-Watt(Discharge): start of frequency drop | 放电过频降有功起始点 | int16 | Hz | Bias from rated frequency | 100 | 0.1-1Hz | 0.1 | Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode. When the actual frequency is above the point, the active power will be regulated(lowered) with the ramp rate In Australia, this register shall be fixed to 0.25Hz
0x0365 | 869 | 869 | 1 | RW | Freq-Watt (Discharge): slope of frequency drop | 放电过频降有功调节斜率 | int16 | %Ppresent/Hz | ratio | 100 | 0.02~0.07 | 0.05 | The ramp rate is defined as multiple of set active power per hertz that above the above the Freq/Watt regulation point. Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode. Example: Rated frequency is 60Hz, the target active power is set to 10kW, Freq/Watt regulation point is set to 2Hz, ramp rate is set as 0.5, If the actual frequency reaches 63Hz, the output active power will be 10kW-(63Hz-62Hz)×0.5*(10kW/Hz) = 5kW
0x0366 | 870 | 870 | 1 | RW | Freq-Watt (Discharge) (Australia only): Fstop-DISCH | 放电过频降有功终点（用于澳洲认证） | int16 | Hz | AS4777 only, bias Bias from rated frequency | 100 | 0.26~3Hz | 2
0x0367 | 871 | 871 | 1 | RW | Freq-Watt(Charge)(Australia only): Fstop-CH | 充电欠频降有功终点（用于澳洲认证） | int16 | Hz | AS4777 only, bias Bias from rated frequency | 100 | -0.26~-4Hz | -1
0x0368 | 872 | 872 | 1 | RW | Volt-Watt (Charge)(Australia only) : Vstart-CH | 充电欠压降有功起始点（用于澳洲认证） | int16 | %Vrated | AS4777 only, ratio | 1000 | 0.900~1.000 | 0.957
0x036C | 876 | 876 | 1 | RW | Soft-start Ramp Rate(SS) | 软启功率变化速率 | int16 | %Prated/s | ratio | 10000 | 0.001~3 | 3 | SS takes effect when the inverter starts, or when the inverter is on "grid reconnection" after the trip caused by FVRT timeout
0x036D | 877 | 877 | 1 | RW | Power Ramp Rate(RR) | 功率变化速率 | int16 | %Prated/s | Enable first | 10000 | 0.001~3 | 3 | RR takes effect in Volt-Watt or Freq-Watt mode when the grid is back to normal state and the inverter tring to go back to normal output. In other words, as long as the inverter doesn’t trip, and the inverter had derated the output power, RR takes effect when the inverter tries to go back to normal output. Available only when Power rising mode is set to ramp mode(53626). If the value is 2.000, which means within 0.5 seconds the system can runs to full power output.
0x036E | 878 | 878 | 1 | RW | Target PF | 目标功率因数 | int16 |  |  | 100 | -1~+1 -: inductive +: capacitve | 1 | Available only when Constant PF is enabled
0x036F | 879 | 879 | 1 | RW | Watt-PF: P1 | 有功调节功率因数: 有功调节点P1 | int16 | %Prated | ratio | 100 | 0.20~1.00 | 0.02 | Available only when active power regulation mode(53636) is set to Freq/Watt and operating in discharge mode. When the actual frequency is above the point, the active power will be regulated(lowered) with the ramp rate
0x0370 | 880 | 880 | 1 | RW | Watt-PF: P2 | 有功调节功率因数: 有功调节点P2 | int16 | %Prated | ratio | 100 | 0.20~1.00 | 0.5
0x0371 | 881 | 881 | 1 | RW | Watt-PF: P3 | 有功调节功率因数: 有功调节点P3 | int16 | %Prated | ratio | 100 | 0.20~1.00 | 0.7
0x0372 | 882 | 882 | 1 | RW | Watt-PF: P4 | 有功调节功率因数: 有功调节点P4 | int16 | %Prated | ratio | 100 | 0.20~1.00 | 1
0x0373 | 883 | 883 | 1 | RW | Watt-PF: PF1 | 有功调节功率因数: 功率因数调节点PF1 | int16 |  |  | 100 | -0.90~0.90 | 1
0x0374 | 884 | 884 | 1 | RW | Watt-PF: PF2 | 有功调节功率因数: 功率因数调节点PF2 | int16 |  |  | 100 | -0.90~0.90 | 1
0x0375 | 885 | 885 | 1 | RW | Watt-PF: PF3 | 有功调节功率因数: 功率因数调节点PF3 | int16 |  |  | 100 | -0.90~0.90 | -0.96
0x0376 | 886 | 886 | 1 | RW | Watt-PF: PF4 | 有功调节功率因数: 功率因数调节点PF4 | int16 |  |  | 100 | -0.90~0.90 | -0.9
0x0377 | 887 | 887 | 1 | RW | continous over voltage trip threshold in 10 minutes | 10分钟连续过压保护幅值 | int16 | %Vrated | ratio | 100 | 1.06~1.12 | 1.1
0x0378 | 888 | 888 | 1 | RW | frequency variation rate trip threshold | 电网频率变化率超额保护阈值 | int16 |  |  |  | 0: disabled 1: rate limit 0.125Hz/s 2: rate limit 0.2Hz/s | 0
0x0379 | 889 | 889 | 1 | RW | Phase angle abrupt trip threshold | 电网相角突变保护阈值 | int16 |  |  |  | 0: disabled， 1: angle abrupt limit 12° 2: angle abrupt limit 6° | 0
0x037A | 890 | 890 | 1 | RW | Grid Reconnection: voltage upper limit | 电网重连上限电压(VDE) | int16 | %Vrated | ratio | 1000 | 1.00~1.15 | 1.1 | Available only when Power rising mode is set to ramp mode . once tripped after FVRT timeout, the inverter can reconnect to the grid when frequency or voltage is back to the thresholds defined as "grid is back to service". In HECO14 /CPUC 21, this register is unnecessary to
0x037B | 891 | 891 | 1 | RW | Grid Reconnection: voltage lower limit | 电网重连下限电压(VDE) | int16 | %Vrated | ratio | 1000 | 0.80~1.00 | 0.85
0x037C | 892 | 892 | 1 | RW | Grid Reconnection: frequency upper limit | 电网重连上限频率 | int16 | Hz | Bias from rated frequency | 100 | 0~0.15Hz | 0.05Hz | Available only when Power rising mode is set to ramp mode once tripped after FVRT timeout, the inverter can reconnect to the grid when frequency or voltage is back to the thresholds defined as "grid is back to service"
0x037D | 893 | 893 | 1 | RW | Grid Reconnection: frequency lower limit | 电网重连下限频率 | int16 | Hz | Bias from rated frequency | 100 | -3~0Hz | -2.5Hz
0x0FA1 | 4001 | 4006 | 6 | W | Time setting - Year\Month\Day\Hour\Minute\Second |  | uint16 | [5 empty] | YYYYMMDDHHmmss
OPTIONAL BMS FORWARDING SECTION- START
0xF001 | 61441 | 61442 | 1 | R | Battery total voltage | 电池总电压 | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF002 | 61442 | 61443 | 1 | R | Battery total current | 电池总电流 | int16 | A |  |  |  |  | BMS protocol for Vendor A
0xF003 | 61443 | 61444 | 1 | R | Battery SOC |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF004 | 61444 | 61445 | 1 | R | Battery SOH |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF005 | 61445 | 61446 | 1 | R | Battery status bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF006 | 61446 | 61447 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF007 | 61447 | 61448 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF008 | 61448 | 61449 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF009 | 61449 | 61450 | 1 | R | Min temperature | 最低温度 | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00A | 61450 | 61451 | 1 | R | Min temperature index | 最低温度指数 | uint16 | [5 empty] | BMS protocol for Vendor A
0xF00B | 61451 | 61452 | 1 | R | Max temperature | 最高温度 | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00C | 61452 | 61453 | 1 | R | Max temperature index | 最高温度指数 | uint16 | [5 empty] | BMS protocol for Vendor A
0xF00D | 61453 | 61454 | 1 | R | Average temperature | 平均温度 | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00E | 61454 | 61455 | 1 | R | Average voltage | 平均电压 | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF00F | 61455 | 61456 | 1 | R | Min voltage | 最小电压 | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF010 | 61456 | 61457 | 1 | R | Min voltage index | 最小电压指数 | uint16 | [5 empty] | BMS protocol for Vendor A
0xF011 | 61457 | 61458 | 1 | R | Max voltage | 最大电压 | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF012 | 61458 | 61459 | 1 | R | Max voltage index | 最大电压指数 | uint16 | [5 empty] | BMS protocol for Vendor A
0xF013 | 61459 | 61460 | 1 | R | Max Allow charge current | 最大允许充电电流 | uint16 | A |  |  |  |  | BMS protocol for Vendor A
0xF014 | 61460 | 61461 | 1 | R | Max Allow discharge current | 最大允许放电电流 | uint16 | A |  |  |  |  | BMS protocol for Vendor A
0xF015 | 61461 | 61462 | 1 | R | BMS firmware version_LMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF016 | 61462 | 61463 | 1 | R | BMS firmware version_BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF017 | 61463 | 61464 | 1 | R | BMS firmware version_Top BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF018 | 61464 | 61465 | 1 | R | BMS hardware version_LMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF019 | 61465 | 61466 | 1 | R | BMS hardware version_BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01A | 61466 | 61467 | 1 | R | BMS hardware version_Top BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01B | 61467 | 61468 | 1 | R | 1~16 Cluster status |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01C | 61468 | 61469 | 1 | R | 17~20 Cluster status |  | uint16 | [5 empty] | BMS protocol for Vendor A
OPTIONAL BMS FORWARDING SECTION- END
0x0260 Operation enum16 list
enum16 | St |  |  |  | OFF | 关机 | 1
enum16 | St |  |  |  | SLEEPING (NOT implemented yet) | 睡眠（未启用） | 2
enum16 | St |  |  |  | STARTING (NOT implemented yet) | 开机中 | 3
enum16 | St |  |  |  | MPPT (NOT implemented yet) | MPPT（未启用） | 4
enum16 | St |  |  |  | THROTTLED | 限流 | 5
enum16 | St |  |  |  | SHUTTING_DOWN (NOT implemented yet) | 关机中 | 6
enum16 | St |  |  |  | FAULT | 故障 | 7
enum16 | St |  |  |  | STANDBY | 待机 | 8
enum16 | St |  |  |  | STARTED | 已启动 | 9
0x0262 Event bitfield32 list
bitfield32 | Evt1 |  |  |  | GROUND_FAULT | 接地故障 | 0
bitfield32 | Evt1 |  |  |  | DC_OVER_VOLT | 直流侧过压 | 1
bitfield32 | Evt1 |  |  |  | AC_DISCONNECT(AC relays open) | AC继电器断开 | 2
bitfield32 | Evt1 |  |  |  | DC_DISCONNECT(DC relays open) | DC继电器断开 | 3
bitfield32 | Evt1 |  |  |  | GRID_DISCONNECT | 电网断开 | 4
bitfield32 | Evt1 |  |  |  | CABINET_OPEN (NOT implemented yet) | 机柜打开（未启用） | 5
bitfield32 | Evt1 |  |  |  | MANUAL_SHUTDOWN | 手动关机 | 6
bitfield32 | Evt1 |  |  |  | OVER_TEMP | 过温 | 7
bitfield32 | Evt1 |  |  |  | OVER_FREQUENCY | 过频 | 8
bitfield32 | Evt1 |  |  |  | UNDER_FREQUENCY | 欠频 | 9
bitfield32 | Evt1 |  |  |  | AC_OVER_VOLT | AC过压 | 10
bitfield32 | Evt1 |  |  |  | AC_UNDER_VOLT | AC欠压 | 11
bitfield32 | Evt1 |  |  |  | BLOWN_STRING_FUSE (NOT implemented yet) | 保险已烧（未启用） | 12
bitfield32 | Evt1 |  |  |  | UNDER_TEMP (NOT implemented yet) | 温度过低（未启用） | 13
bitfield32 | Evt1 |  |  |  | MEMORY_LOSS | 内存错误 | 14
bitfield32 | Evt1 |  |  |  | HW_TEST_FAILURE (NOT implemented yet) | 硬件检测失败（未启用） | 15
Note on A309: The decade value of this register indcates the status
Note on A320: The decade value of this register indcates the status

## Status and Fault List
Address （DEC） | Flags | Flag category | Flag name in Chinese | value
32 | Bit0 Fault status | Fault | 故障: 故障综合 | 0: False, 1:ture
32 | Bit1 Alert status | Warning | 告警: 告警综合 | 0: False, 1:ture
32 | Bit2 On/Off status | Status | 状态: 已开机 | 0: False, 1:ture
32 | Bit3 On-grid | Status | 状态: 并网 | 0: False, 1:ture
32 | Bit4 Off-grid(Island mode) | Status | 状态: 离网 | 0: False, 1:ture
32 | Bit5 Reserved
32 | Bit6 Reserved
32 | Bit7 Reserved
32 | Bit8-15 Reserved
33 | Bit0-7 Reserved
33 | Bit8 anti-islanding function enabled | Status | 状态: 孤岛保护使能 | 0: False, 1:ture
33 | Bit9-15 Reserved
34 | Bit0-7 Reserved
34 | Bit8-15 Reserved
35 | Bit0-7 Reserved
35 | Bit8-15 Reserved
36 | bit0 AC OVP | Warning | 告警: 交流侧过压保护 | 0: False, 1:ture
36 | Bit1 AC UVP | Warning | 告警: 交流侧欠压保护 | 0: False, 1:ture
36 | Bit2 AC OFP | Warning | 告警: 交流侧过频保护 | 0: False, 1:ture
36 | Bit3 AC UFP | Warning | 告警: 交流侧欠频保护 | 0: False, 1:ture
36 | Bit4 Grid voltage unbalance. | Warning | 告警: 电网电压不平衡 | 0: False, 1:ture
36 | Bit5 Grid phase reverse | Warning | 告警: 电网电压反序 | 0: False, 1:ture
36 | Bit6 Anti-islanding scheme taking effect (and grid is out) | Status | 状态: 孤岛状态 | 0: False, 1:ture
36 | Bit7 On/off-grid switching error | Warning | 告警: 并离网切换故障 | 0: False, 1:ture
36 | Bit8 Output grounding error | Fault | 故障: 输出接地故障 | 0: False, 1:ture
36 | Bit9 Reserved
36 | Bit10 Grid phase lock failed | Warning | 告警: 电网锁相失败 | 0: False, 1:ture
36 | Bit11 Internal air over-temp | Warning | 告警: 内部环境温度过温 | 0: False, 1:ture
36 | Bit12 Enabling grid-tieing criterion detecting timeout | Status | 状态: 并网条件判断超时使能 | 0: False, 1:ture
36 | Bit13-15 Reserved
37 | Bit0 EPO(Emergency Power-off) tripping | Warning | 告警: 急停按钮被按下 | 0: False, 1:ture
37 | bit1 HMI parameters fault | Fault | 故障: 监控参数故障 | 0: False, 1:ture
37 | Bit2 DSP version error | Fault | 故障: DSP软件版本错误 | 0: False, 1:ture
37 | Bit3 CPLD version error | Fault | 故障: CPLD软件版本错误 | 0: False, 1:ture
37 | Bit4 Hardware Version error | Fault | 故障: 硬件版本错误 | 0: False, 1:ture
37 | Bit5 Communication error | Fault | 故障: 通讯错误 | 0: False, 1:ture
37 | Bit6 Aux power error | Fault | 故障: 辅助电源错误 | 0: False, 1:ture
37 | Bit7-Fan failure | Fault | 故障: 风扇故障 | 0: False, 1:ture
37 | Bit8 BUS over voltage | Warning | 告警: 母线电压过压 | 0: False, 1:ture
37 | Bit9 BUS low voltage | Warning | 告警: 母线电压欠压 | 0: False, 1:ture
37 | Bit10 BUS voltage unbanlaced | Warning | 告警: 母线电压不平衡 | 0: False, 1:ture
37 | Bit11 reserved
37 | Bit12 Reserved
37 | Bit13 Output voltage abnormal. | Fault | 故障: 输出电压异常 | 0: False, 1:ture
37 | Bit14 Output current unbalanced | Fault | 故障: 输出电流不平衡 | 0: False, 1:ture
37 | Bit15 Over-temperature of heat sink | Warning | 告警: 散热器过温 | 0: False, 1:ture
38 | Bit0 Output Overload | Warning | 告警: 输出过载 | 0: False, 1:ture
38 | Bit1 Reserved |  |  | 0: False, 1:ture
38 | Bit2 AC relay short-circuit. | Fault | 故障: AC继电器短路 | 0: False, 1:ture
38 | Bit3 Inverter start failure. | Fault | 故障: 逆变器启动失败 | 0: False, 1:ture
38 | Bit4 AC relay is open. | Fault | 故障: AC继电器开路 | 0: False, 1:ture | AC switch S2
38 | Bit5-15 Reserved |  |  | 0: False, 1:ture
39 | Bit0 EE Reading error 1 | Fault | 故障: EE读取错误1 | 0: False, 1:ture
39 | Bit1 EE Reading error 2 | Fault | 故障: EE读取错误2 | 0: False, 1:ture
39 | Bit2 Reserved
39 | Bit3 Inverter over load | Warning | 告警: 逆变器过载 | 0: False, 1:ture
39 | Bit4-15 Reserved
40 | bit0 DC charging | Status | 状态: DC充电中 | 0: False, 1:ture
40 | bit1 DC discharging | Status | 状态: DC放电中 | 0: False, 1:ture
40 | bit2 Battery fully charged | Status | 状态: 电池充满 | 0: False, 1:ture
40 | bit3-Battery empty | Status | 状态: 电池放空 | 0: False, 1:ture
40 | Bit4 Reserved
40 | Bit5 Reserved
40 | Bit6-15 Reserved
41 | Bit0-7 Reserved
41 | Bit8-15 Reserved
42 | Bit0-7 Reserved
42 | Bit8-15 Reserved
43 | Bit0-7 Reserved
43 | Bit8-15 Reserved
44 | Bit0 DC input OVP(over voltage protection) | Warning | 告警: DC输入过压保护 | 0: False, 1:ture
44 | Bit1 DC input UVP(under voltage protection) | Warning | 告警: DC输入欠压保护 | 0: False, 1:ture
44 | Bit2 reserved
44 | Bit3 BMS Alerts.(available only BMS connected) | Warning | 告警: BMS告警 | 0: False, 1:ture
44 | Bit4-7 Reserved |  |  | 0: False, 1:ture
44 | Bit8-15 Reserved |  |  | 0: False, 1:ture
45 | bit0 DC soft-start failed. | Warning | 告警: DC软起动失败 | 0: False, 1:ture
45 | bit1 DC relay short-circuit. | Fault | 故障: DC继电器短路 | 0: False, 1:ture
45 | bit2 DC relay short-open | Fault | 故障: DC继电器开路 | 0: False, 1:ture
45 | Bit3 Battery power over load. |  |  | 0: False, 1:ture
45 | Bit4 DC BUS starting failed | Warning | 告警: 母线启动失败 | 0: False, 1:ture
45 | Bit5-7 Reserved
45 | Bit8-15 Reserved
46 | Bit0-7 Reserved
46 | Bit8-15 Reserved
47 | Bit0 DC OCP | Warning | 告警: DC过流保护 | 0: False, 1:ture
47 | Bit1-7 Reserved
47 | Bit8-15 Reserved
48-63 | Reserved

## Fault code on LCD of PWS2-30M
| Fault Code | Fault | Fault in Chinese
0 | 0 | AC overvoltage | 交流过压
1 | 1 | AC undervoltage | 交流欠压
2 | 2 | AC overfrequency | 交流过频
3 | 3 | AC underfrequency | 交流欠频
4 | 4 | Grid voltage asymmetric | 电网电压不平衡
5 | 5 | Phase reversed | 电网反序
6 | 6 | Inverter detects islanding | 逆变器孤岛
7 | 7 | Grid interconnection toggle failed | 并离网切换异常
8 | 8 | Ground fault | 输出接地故障
9 | 9 | PPL failed | 电网锁相失败
10 | A | Internal over temperature | 内部环境温度过温
11 | B | Grid checking timeout | 电网检测超时
12 | C
13 | D
14 | E
15 | F
16 | 10 | Emergency power off | EPO
17 | 11 | Wrong parameter set | 监控参数设置故障
18 | 12 | DSP version fault | DSP 版本故障
19 | 13 | CPLD version fault | CPLD版本故障
20 | 14 | Hardware version fault | 硬件版本故障
21 | 15 | CAN communication failed | CAN 通信故障
22 | 16 | Auxiliary power down | 辅助电源故障
23 | 17 | Fan failed | 风扇故障 ,
24 | 18 | DC link overvoltage | 母线电压高
25 | 19 | DC link undervoltage | 母线电压低
26 | 1A | DC link voltage unbalanced | 母线电压不平衡
27 | 1B
28 | 1C |  | 交流继电器短路
29 | 1D | Abnormal output voltages | 输出电压异常
30 | 1E | Asymmetric current outputs | 输出电流不平衡
31 | 1F | Heatsink overheated | 散热器过温
32 | 20 | Overloaded timeout | 输出过载超时
33 | 21 | Grid countineously overvoltage | 电网连续过压
34 | 22 | AC precharge failed | 交流软启动失败
35 | 23 | failed to start inverting | 逆变启动失败
36 | 24 | AC relay open | 交流继电器开路
37 | 25 | Communication fault to secondary CPU | U2板通信故障
38 | 26 | Too much DC component | AC 直流分量超额
39 | 27 | Master-slave sampling abnormal | 主从采样异常
40 | 28 | EEPROM reading error 1 | EE读取错误 1
41 | 29 | EEPROM reading error 2 | EE读取错误 2
42 | 2A | EEPROM reading error 3 | EE读取错误 3
43 | 2B |  | 逆变器过载
44 | 2C
45 | 2D
46 | 2E
47 | 2F
48 | 30
49 | 31
50 | 32
51 | 33
52 | 34
53 | 35
54 | 36
55 | 37
56 | 38 |  | 直流输入过压
57 | 39 |  | 直流输入欠压
58 | 3A |  | 直流接地故障
59 | 3B |  | BMS告警
60 | 3C |  | BMS连接超时
61 | 3D |  | EMS连接超时
62 | 3E
63 | 3F
64 | 40 |  | 直流软启动失败
65 | 41 |  | 直流继电器短路
66 | 42 |  | 直流继电器开路
67 | 43 |  | 电池功率过载超时
68 | 44 |  | 母线软启动失败
69 | 45 |  | 直流快检过流
70 | 46
71 | 47
72 | 48 |  | 直流电流过流
| 90 |  | 参数下设错误
| 91 |  | 离网能量低
| 92 |  | N线未链接
| 93 |  | 待机母线高
| 95 |  | 频率变化率超额
| 96 |  | 电网相角突变故障

## Specified BMS Protocol
| Start | End | Size | Access | Register Name | Type | Units | Comments | remarks
0x00A8 | 168 | 168 | 1 | W | D.C._Voltage | uint16 | V | D.C. Voltage | BMS protocol for Vendor B
0x00A9 | 169 | 169 | 1 | W | D.C._Voltage_SF | sunssf | SF | D.C. Voltage SF | BMS protocol for Vendor B
0x00AA | 170 | 170 | 1 | W | D.C._Current | uint16 | A | D.C. Current | BMS protocol for Vendor B
0x00AB | 171 | 171 | 1 | W | D.C._Current_SF | sunssf | SF | D.C. Current SF | BMS protocol for Vendor B
0x00AC | 172 | 172 | 1 | W | average_temp | uint16 | C | average temp | BMS protocol for Vendor B
0x00AD | 173 | 173 | 1 | W | average_temp_SF | sunssf | SF | average temp SF | BMS protocol for Vendor B
0x00AE | 174 | 174 | 1 | W | max_temp | uint16 | C | max temp | BMS protocol for Vendor B
0x00AF | 175 | 175 | 1 | W | max_temp_SF | sunssf | SF | max temp SF | BMS protocol for Vendor B
0x00B0 | 176 | 176 | 1 | W | min_Temp | uint16 | C | min Temp | BMS protocol for Vendor B
0x00B1 | 177 | 177 | 1 | W | min_Temp_SF | sunssf | SF | min Temp SF | BMS protocol for Vendor B
0x00B2 | 178 | 178 | 1 | W | max_cell_volt | uint16 | V | max cell volt | BMS protocol for Vendor B
0x00B3 | 179 | 179 | 1 | W | max_cell_volt_SF | sunssf | SF | max cell volt SF | BMS protocol for Vendor B
0x00B4 | 180 | 180 | 1 | W | min_cell_volt | uint16 | V | min cell volt | BMS protocol for Vendor B
0x00B5 | 181 | 181 | 1 | W | min_cell_volt_SF | sunssf | SF | min cell volt SF | BMS protocol for Vendor B
0x00B6 | 182 | 182 | 1 | W | average_cell_volt | uint16 | V | average cell volt | BMS protocol for Vendor B
0x00B7 | 183 | 183 | 1 | W | average_cell_volt_SF | sunssf | SF | average cell volt SF | BMS protocol for Vendor B
0x00B8 | 184 | 184 | 1 | W | soc | uint16 |  | soc | BMS protocol for Vendor B
0x00B9 | 185 | 185 | 1 | W | soc_SF | sunssf | SF | soc SF | BMS protocol for Vendor B
0x00BA | 186 | 186 | 1 | W | soh | uint16 |  | soh | BMS protocol for Vendor B
0x00BB | 187 | 187 | 1 | W | soh_SF | sunssf | SF | soh SF | BMS protocol for Vendor B
0xF001 | 61441 | 61442 | 1 | W | Battery total voltage | uint16 | V |  | BMS protocol for Vendor A
0xF002 | 61442 | 61443 | 1 | W | Battery total current | int16 | A |  | BMS protocol for Vendor A
0xF003 | 61443 | 61444 | 1 | W | Battery SOC | uint16 |  |  | BMS protocol for Vendor A
0xF004 | 61444 | 61445 | 1 | W | Battery SOH | uint16 |  |  | BMS protocol for Vendor A
0xF005 | 61445 | 61446 | 1 | W | Battery status bits | uint16 |  |  | BMS protocol for Vendor A
0xF006 | 61446 | 61447 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF007 | 61447 | 61448 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF008 | 61448 | 61449 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF009 | 61449 | 61450 | 1 | W | Min temperature | int16 | C |  | BMS protocol for Vendor A
0xF00A | 61450 | 61451 | 1 | W | Min temperature index | uint16 |  |  | BMS protocol for Vendor A
0xF00B | 61451 | 61452 | 1 | W | Max temperature | int16 | C |  | BMS protocol for Vendor A
0xF00C | 61452 | 61453 | 1 | W | Max temperature index | uint16 |  |  | BMS protocol for Vendor A
0xF00D | 61453 | 61454 | 1 | W | Average temperature | int16 | C |  | BMS protocol for Vendor A
0xF00E | 61454 | 61455 | 1 | W | Average voltage | uint16 | V |  | BMS protocol for Vendor A
0xF00F | 61455 | 61456 | 1 | W | Min voltage | uint16 | V |  | BMS protocol for Vendor A
0xF010 | 61456 | 61457 | 1 | W | Min voltage index | uint16 |  |  | BMS protocol for Vendor A
0xF011 | 61457 | 61458 | 1 | W | Max voltage | uint16 | V |  | BMS protocol for Vendor A
0xF012 | 61458 | 61459 | 1 | W | Max voltage index | uint16 |  |  | BMS protocol for Vendor A
0xF013 | 61459 | 61460 | 1 | W | Max Allow charge current | uint16 | A |  | BMS protocol for Vendor A
0xF014 | 61460 | 61461 | 1 | W | Max Allow discharge current | uint16 | A |  | BMS protocol for Vendor A
0xF015 | 61461 | 61462 | 1 | W | BMS firmware version_LMU | uint16 |  |  | BMS protocol for Vendor A
0xF016 | 61462 | 61463 | 1 | W | BMS firmware version_BMU | uint16 |  |  | BMS protocol for Vendor A
0xF017 | 61463 | 61464 | 1 | W | BMS firmware version_Top BMU | uint16 |  |  | BMS protocol for Vendor A
0xF018 | 61464 | 61465 | 1 | W | BMS hardware version_LMU | uint16 |  |  | BMS protocol for Vendor A
0xF019 | 61465 | 61466 | 1 | W | BMS hardware version_BMU | uint16 |  |  | BMS protocol for Vendor A
0xF01A | 61466 | 61467 | 1 | W | BMS hardware version_Top BMU | uint16 |  |  | BMS protocol for Vendor A
0xF01B | 61467 | 61468 | 1 | W | 1~16 Cluster status | uint16 |  |  | BMS protocol for Vendor A
0xF01C | 61468 | 61469 | 1 | W | 17~20 Cluster status | uint16 |  |  | BMS protocol for Vendor A
BMS frame format
BMS communication mplementing RS485, the baud rate is 19200bps or 9600bps(default), verification: Modbus RTU Crc16
Intro The registers listed in this table, is used for those BMS developers who are willing to make there BMS messages to be adapted to the inverter. These registers are to be written by BMS via RS485, in this case, the EMS can only use Ethernet as the communication method.
Vendor B protocol is only for transferring the data from BMS via RS485 to EMS via Ethernet, no protection will be applied by inverter. Vendor A protocol provides protection and status display by inverter Protocol for Vendor A is Strongly RECOMMENDED
SF(Scale Factor) is defined by Sunspec & MESA Actual value= Register value×10(SF)
Sending broadcasting frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x00 | 0x06 | 0x00 | 0xA8 | 0x00 | 0x03 | CRC
THERE WILL BE NO Response frame